## Guide
راهنمای بانک قیمت پمپ – نسخه ۸
بر اساس شرح نیاز و اصلاحات سازمانی مهر ۱۴۰۵
ترتیب ستون‌ها | شناسایی ← مشخصات کلیدی (نوع و متریال API 610، دبی، هد، توان، استانداردها، آب‌بند) ← مشخصات تکمیلی ← قیمت ← دامنه کار ← منبع ← محاسبات ← کنترل. ستون‌های فرعی گروه‌بندی شده‌اند و با «+» بالای ستون باز می‌شوند.
رنگ‌ها | سرستون زرد = ورودی Dropdown؛ آبی روشن = ورودی آزاد؛ خاکستری = فرمول. سلول زرد پررنگ = مقدار استنباطی (شاهد در Note). سلول آبی در ستون IRR = تبدیل با نرخ بانک؛ نرخ و قیمت پروژه در Note.
Standards | ستون Standards خودکار از ستون‌های جمع‌شده Pump Standard، IPS، NACE و NFPA 20 ساخته می‌شود. ورودی‌ها را در همان ستون‌های جمع‌شده تغییر دهید.
نرمال‌سازی | Normalized EUR = قیمت یورویی سال منبع ÷ (MAT × SEAL × DRIVE × SCOPE) = قیمت معادل پیکربندی پایه. ضرایب در Factors_ROT و هنوز کالیبره نشده‌اند.
تعدیل | یورو × PPI(هدف)/PPI(پایه)، با کف ۲۵٬۰۰۰ یورو (۱۴۰۴) برای API 610 گریز از مرکز کلاس S/D؛ دلار و ریال با نرخ‌های سال هدف. شاخص PPI از Eurostat C28.13 (EA20)؛ عدد ۱۴۰۵ پیش‌بینی است. CPI استفاده نمی‌شود.
Price Basis چیست؟ | ستون Price Basis می‌گوید عدد قیمت «چه نوع قیمتی» است و از کدام سند آمده: پیشنهاد فروشنده (Inquiry)، برآورد مشاور در MTO مرحله FEED یا Basic، یا قیمت خرید. برچسب کلاس برآورد که در خود سند منبع نوشته شده، عیناً داخل همین متن آمده است.
Incoterm چیست؟ | ستون Incoterm شرط تحویل قیمت است (EXW، FOB و ...). Note هر سلول صریحاً می‌گوید این قیمت «شامل» چه هزینه‌هایی هست و «شامل» چه هزینه‌هایی نیست (حمل، بیمه، ترخیص، بازرسی، یدکی، سربار، مالیات، نصب) و هر کدام در کدام سلول سند منبع جداگانه آمده است. جدول معرفی حالت‌ها در Executive Dashboard است.
یعنی چه قیمتی می‌بینیم؟ | Unit Price (Reference) و معادل‌های یورو/دلار/ریال سال منبع = قیمت تجهیز در سطح فروشنده، بدون سربار پروژه، مالیات و نصب (جز آنچه Note همان ردیف خلاف آن را بگوید). قیمت‌های Escalated همان قیمت است که فقط از نظر زمان به سال هدف آورده شده؛ هیچ هزینه دیگری به آن اضافه نشده است.
Estimator | پارامترها در سمت چپ با ضریب متناظر در ستون C؛ محاسبات و نتیجه در پنل سمت راست.
Search | فیلترها در سه بلوک بالا؛ خلاصه نتایج و لیست رکوردها زیر آن.
Vendor_Quotes | سند پیوست استعلام‌ها؛ در محاسبات Master استفاده نمی‌شود.
رکورد جدید | آخرین ردیف Master را کپی و زیر آن Paste کنید تا فرمول‌ها منتقل شوند (Dropdownها تا ردیف ۶۰۰).

## Executive Dashboard
EXECUTIVE DASHBOARD – بانک قیمت پمپ
فقط رکوردهای Include = Y شمارش می‌شوند. روی سرستون‌ها و سلول‌ها Note توضیحی یا ترجمه فارسی هست.
Target year | 1404 | EUR→IRR | 695268 | USD→IRR | 658533 | PPI target | 123.416
1) Pump sub-categories
Sub-Category | Full Name | شرح | Records | With escalated price | % Material stated | % Seal stated | % Size driver
ROT-CRU | Crude Oil & Main Transfer Pumps | پمپ‌های نفت خام: انتقال نفت شور و نمک‌زدایی‌شده، Booster، Off-spec و انتقال اصلی | 15 | 10 | 46.67% | 0% | 93.33%
ROT-WAT | Desalting & Process Water Pumps | آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن | 36 | 28 | 66.67% | 0% | 91.67%
ROT-INJ | Produced Water & Disposal Injection Pumps | آب تولیدی و پساب: Booster و پمپ‌های پرفشار تزریق به چاه دفعی | 21 | 15 | 80.95% | 0% | 76.19%
ROT-DRN | Drainage, Flare & OWS Pumps | درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن | 33 | 27 | 75.76% | 0% | 63.64%
ROT-AUX | Chemical, Fuel & Auxiliary Pumps | پمپ‌های جانبی: مواد شیمیایی، گلایکول، گازوئیل و سوخت | 11 | 9 | 63.64% | 0% | 54.55%
ROT-FIR | Firewater & Safety Pumps | آتش‌نشانی: پمپ اصلی برقی و دیزلی، Jockey و بارگیری آب آتش‌نشانی | 16 | 16 | 75% | 0% | 100%
TOTAL |  |  | 132 | 105 | 69.7% | 0% | 80.3%
2) API 610 material classes (Table H.1)
Class | Casing | Impeller | Wear rings / Shaft | Typical service
I-1 | Cast iron | Cast iron | Cast-iron rings; carbon-steel shaft | Water and non-corrosive services, low temperature
I-2 | Cast iron | Bronze | Bronze rings; carbon-steel shaft | Water, fire water, fresh water
S-1 | Carbon steel | Cast iron | Cast-iron rings; carbon-steel shaft | Non-corrosive hydrocarbons
S-3 | Carbon steel | Ni-resist | Ni-resist rings; AISI 4140 shaft | Mildly abrasive or corrosive services
S-4 | Carbon steel | Carbon steel | Cast-iron rings; carbon-steel shaft | General hydrocarbons
S-5 | Carbon steel | Carbon steel | Hardened 12% Cr rings; AISI 4140 shaft | General and hot hydrocarbons
S-6 | Carbon steel | 12% Cr | Hardened 12% Cr rings; 12% Cr shaft | Hot hydrocarbons, sour water, mild corrosion
S-8 | Carbon steel | 316 stainless steel | Hard-faced 316 rings; 316 shaft | More corrosive services
S-9 | Carbon steel | Ni-Cu alloy | Ni-Cu rings; Ni-Cu shaft | Special corrosive services
C-6 | 12% Cr | 12% Cr | Hardened 12% Cr rings; 12% Cr shaft | Boiler feed water, hot hydrocarbons
A-7 | Austenitic stainless steel | Austenitic stainless steel | Hard-faced rings; austenitic shaft | High corrosion, low temperature
A-8 | 316 stainless steel | 316 stainless steel | Hard-faced rings; 316 shaft | Corrosive services
D-1 | Duplex stainless steel | Duplex stainless steel | Hard-faced rings; duplex shaft | Saline and produced water with chlorides
D-2 | Super-duplex stainless steel | Super-duplex stainless steel | Hard-faced rings; super-duplex shaft | High-chloride saline / produced water, severe corrosion
SS316L (non-API) | 316L stainless steel | 316L stainless steel | — | Non-API construction (e.g. portable barrel pump)
Not stated | — | — | — | Not stated in source
3) Pump types per API 610
Type | Name | Description
OH1 | Overhung, foot-mounted | Single-stage overhung, foot-mounted; moderate temperature and pressure
OH2 | Overhung, centreline-mounted | Single-stage overhung, centreline-mounted; the most common refinery process pump, suitable for high temperature
OH3 | Vertical in-line, separate bearing bracket | Vertical in-line pump with separate bearing bracket
OH4 | Vertical in-line, rigidly coupled | Vertical in-line pump, rigidly coupled
OH5 | Vertical in-line, close-coupled | Vertical in-line pump, close-coupled (impeller on the motor shaft)
OH6 | High-speed integral gear | High-speed integral-gear pump; low flow, high head
BB1 | Between bearings, 1–2 stage, axially split | Between bearings, 1–2 stage, axially split casing
BB2 | Between bearings, 1–2 stage, radially split | Between bearings, 1–2 stage, radially split; high temperature and pressure
BB3 | Between bearings, multistage, axially split | Multistage, axially split casing; water injection and high-pressure transfer
BB4 | Between bearings, multistage, single casing radially split | Multistage single-casing ring-section pump
BB5 | Between bearings, multistage, double casing (barrel) | Multistage double-casing (barrel) pump; the most severe high-pressure services
VS1 | Vertically suspended, diffuser, discharge through column | Wet-pit vertically suspended, diffuser, discharge through the column
VS2 | Vertically suspended, volute, discharge through column | Wet-pit vertically suspended, volute, discharge through the column
VS3 | Vertically suspended, axial flow | Wet-pit vertically suspended, axial flow; high flow, low head
VS4 | Vertically suspended, line-shaft, separate discharge (sump) | Line-shaft sump pump with separate discharge; drain and flare KO sumps
VS5 | Vertically suspended, cantilever sump | Cantilever sump pump without submerged bearings
VS6 | Vertically suspended, double casing, diffuser (can) | Double-casing diffuser (can) pump; low NPSH, e.g. off-spec crude and near-boiling liquids
VS7 | Vertically suspended, double casing, volute | Double-casing volute pump
OH (unspecified) | Overhung – subtype not stated | Source states only "Overhung"; API subtype not given
BB (unspecified) | Between bearings – subtype not stated | Source states only "Between Bearings"; API subtype not given
VS (unspecified) | Vertically suspended – subtype not stated | Source states only "Vertical"; API subtype not given
N/A (non-API 610) | Not an API 610 pump | Not an API 610 pump (ISO 5199, NFPA 20, JIS, positive-displacement or portable pump); API 610 type does not apply
Not stated | — | Pump type not stated in source
4) Incoterm – delivery basis of prices
Incoterm | Meaning | توضیح فارسی | Used in this bank for
EXW | Ex Works – goods made available at the seller's works; buyer bears all transport, insurance, export/import costs | تحویل درب کارخانه؛ همه هزینه‌های حمل، بیمه، گمرک و ترخیص با خریدار | گچساران ۴ (هزینه حمل، بیمه، بازرسی و یدکی جدا) و اقلام ریالی کوپال
FCA | Free Carrier – delivered to the buyer's carrier at a named place | تحویل به حمل‌کننده خریدار در محل تعیین‌شده | —
FOB | Free On Board – loaded on the vessel at the port of shipment; sea freight, insurance and import costs for buyer | تحویل روی کشتی در بندر مبدأ؛ کرایه حمل دریایی، بیمه و هزینه‌های ورود با خریدار | پازنان ۲ (۱۳۹۳ و ۱۴۰۴) و اقلام ارزی کوپال
CFR | Cost and Freight – seller pays sea freight to the destination port; insurance for buyer | فروشنده کرایه حمل تا بندر مقصد را می‌پردازد؛ بیمه با خریدار | —
CIF | Cost, Insurance and Freight – seller pays sea freight and minimum insurance to the destination port | فروشنده کرایه حمل و بیمه تا بندر مقصد را می‌پردازد | —
DAP | Delivered At Place – delivered at the named destination, not unloaded; import duties for buyer | تحویل در مقصد تعیین‌شده (مثلاً سایت)؛ حقوق ورودی و ترخیص با خریدار | —
DDP | Delivered Duty Paid – delivered at destination with all duties paid by the seller | تحویل در مقصد با پرداخت همه عوارض و حقوق گمرکی توسط فروشنده | —
Domestic Delivered (IRR) | Domestic supply in rials, delivered to site | خرید داخلی ریالی با تحویل در سایت | —
Not stated | Delivery basis not stated in the source | شرط تحویل در منبع ذکر نشده است | رکوردهای CSV و نمونه قیمتی (بدون پروژه و سال)
در همه رکوردها قیمت در سطح فروشنده است: سربار پروژه، مالیات بر ارزش افزوده و هزینه نصب در هیچ قیمتی نیست. آنچه هر قیمت دقیقاً شامل هست یا نیست، در Note ستون Incoterm همان ردیف در Master Database آمده است.
Note on A4: سال هدف تعدیل (قابل تغییر در شیت Assumptions & FX Reference، سلول I5).
Note on C4: نرخ یوروی سال هدف که در تعدیل استفاده می‌شود.
Note on E4: نرخ دلار سال هدف.
Note on G4: شاخص قیمت تولیدکننده پمپ منطقه یورو (Eurostat C28.13، 2021=100) برای سال هدف.
Note on A6: ۱) زیرگروه‌های پمپ
Note on A7: کد زیرگروه
Note on B7: نام کامل زیرگروه
Note on C7: شرح فارسی و نمونه سرویس‌ها
Note on D7: تعداد رکوردهای Include = Y
Note on E7: تعداد رکوردهایی که قیمت تعدیل‌شده به سال هدف دارند (قیمت، سال، نرخ ارز و PPI موجود).
Note on F7: درصد رکوردهایی که کلاس متریال API 610 آن‌ها مشخص است.
Note on G7: درصد رکوردهایی که نوع آب‌بند (Seal Arrangement) آن‌ها مشخص است.
Note on H7: درصد رکوردهایی که اندازه (kW، از منبع یا محاسبه Q×H) دارند؛ مبنای مقایسه و Estimator.
Note on A16: ۲) کلاس‌های متریال API 610 (جدول H.1)
Note on A17: کلاس متریال
Note on B17: بدنه
Note on C17: پروانه
Note on D17: رینگ سایشی / شفت
Note on E17: کاربرد معمول – راهنمایی کلی؛ انتخاب نهایی طبق API 610 Annex G/H و شرایط سیال
Note on A18: I-1: بدنه چدن، پروانه چدن؛ رینگ چدن؛ شفت فولاد کربنی. کاربرد معمول: آب و سرویس غیرخورنده، دمای پایین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on B18: چدن
Note on C18: چدن
Note on D18: رینگ چدن؛ شفت فولاد کربنی
Note on E18: آب و سرویس غیرخورنده، دمای پایین
Note on A19: I-2: بدنه چدن، پروانه برنز؛ رینگ برنز؛ شفت فولاد کربنی. کاربرد معمول: آب، آب آتش‌نشانی و آب شیرین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on B19: چدن
Note on C19: برنز
Note on D19: رینگ برنز؛ شفت فولاد کربنی
Note on E19: آب، آب آتش‌نشانی و آب شیرین
Note on A20: S-1: بدنه فولاد کربنی، پروانه چدن؛ رینگ چدن؛ شفت فولاد کربنی. کاربرد معمول: هیدروکربن غیرخورنده. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on B20: فولاد کربنی
Note on C20: چدن
Note on D20: رینگ چدن؛ شفت فولاد کربنی
Note on E20: هیدروکربن غیرخورنده
Note on A21: S-3: بدنه فولاد کربنی، پروانه نی‌رزیست (چدن آلیاژی نیکل‌دار)؛ رینگ نی‌رزیست؛ شفت AISI 4140. کاربرد معمول: سرویس‌های با سایش یا خوردگی ملایم. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on B21: فولاد کربنی
Note on C21: نی‌رزیست (چدن آلیاژی نیکل‌دار)
Note on D21: رینگ نی‌رزیست؛ شفت AISI 4140
Note on E21: سرویس‌های با سایش یا خوردگی ملایم
Note on A22: S-4: بدنه فولاد کربنی، پروانه فولاد کربنی؛ رینگ چدن؛ شفت فولاد کربنی. کاربرد معمول: هیدروکربن عمومی. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on B22: فولاد کربنی
Note on C22: فولاد کربنی
Note on D22: رینگ چدن؛ شفت فولاد کربنی
Note on E22: هیدروکربن عمومی
Note on A23: S-5: بدنه فولاد کربنی، پروانه فولاد کربنی؛ رینگ کروم ۱۲٪ سخت‌شده؛ شفت AISI 4140. کاربرد معمول: هیدروکربن عمومی و داغ. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on B23: فولاد کربنی
Note on C23: فولاد کربنی
Note on D23: رینگ کروم ۱۲٪ سخت‌شده؛ شفت AISI 4140
Note on E23: هیدروکربن عمومی و داغ
Note on A24: S-6: بدنه فولاد کربنی، پروانه کروم ۱۲٪؛ رینگ کروم ۱۲٪ سخت‌شده؛ شفت کروم ۱۲٪. کاربرد معمول: هیدروکربن داغ، آب ترش و خوردگی ملایم. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on B24: فولاد کربنی
Note on C24: کروم ۱۲٪
Note on D24: رینگ کروم ۱۲٪ سخت‌شده؛ شفت کروم ۱۲٪
Note on E24: هیدروکربن داغ، آب ترش و خوردگی ملایم
Note on A25: S-8: بدنه فولاد کربنی، پروانه فولاد ضدزنگ 316؛ رینگ 316 با روکش سخت؛ شفت 316. کاربرد معمول: سرویس‌های خورنده‌تر. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on B25: فولاد کربنی
Note on C25: فولاد ضدزنگ 316
Note on D25: رینگ 316 با روکش سخت؛ شفت 316
Note on E25: سرویس‌های خورنده‌تر
Note on A26: S-9: بدنه فولاد کربنی، پروانه آلیاژ نیکل‌-مس؛ رینگ نیکل‌-مس؛ شفت نیکل‌-مس. کاربرد معمول: سرویس‌های خاص خورنده. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on B26: فولاد کربنی
Note on C26: آلیاژ نیکل‌-مس
Note on D26: رینگ نیکل‌-مس؛ شفت نیکل‌-مس
Note on E26: سرویس‌های خاص خورنده
Note on A27: C-6: بدنه کروم ۱۲٪، پروانه کروم ۱۲٪؛ رینگ کروم ۱۲٪ سخت‌شده؛ شفت کروم ۱۲٪. کاربرد معمول: آب داغ (تغذیه بویلر) و هیدروکربن داغ. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on B27: کروم ۱۲٪
Note on C27: کروم ۱۲٪
Note on D27: رینگ کروم ۱۲٪ سخت‌شده؛ شفت کروم ۱۲٪
Note on E27: آب داغ (تغذیه بویلر) و هیدروکربن داغ
Note on A28: A-7: بدنه فولاد ضدزنگ آستنیتی، پروانه فولاد ضدزنگ آستنیتی؛ رینگ با روکش سخت؛ شفت آستنیتی. کاربرد معمول: خوردگی بالا و دمای پایین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on B28: فولاد ضدزنگ آستنیتی
Note on C28: فولاد ضدزنگ آستنیتی
Note on D28: رینگ با روکش سخت؛ شفت آستنیتی
Note on E28: خوردگی بالا و دمای پایین
Note on A29: A-8: بدنه فولاد ضدزنگ 316، پروانه فولاد ضدزنگ 316؛ رینگ با روکش سخت؛ شفت 316. کاربرد معمول: سرویس‌های خورنده. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on B29: فولاد ضدزنگ 316
Note on C29: فولاد ضدزنگ 316
Note on D29: رینگ با روکش سخت؛ شفت 316
Note on E29: سرویس‌های خورنده
Note on A30: D-1: بدنه داپلکس، پروانه داپلکس؛ رینگ با روکش سخت؛ شفت داپلکس. کاربرد معمول: آب شور و آب تولیدی دارای کلراید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on B30: داپلکس
Note on C30: داپلکس
Note on D30: رینگ با روکش سخت؛ شفت داپلکس
Note on E30: آب شور و آب تولیدی دارای کلراید
Note on A31: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on B31: سوپرداپلکس
Note on C31: سوپرداپلکس
Note on D31: رینگ با روکش سخت؛ شفت سوپرداپلکس
Note on E31: آب شور و تولیدی با کلراید بالا و خوردگی شدید
Note on A32: SS316L (non-API): بدنه فولاد ضدزنگ 316L، پروانه فولاد ضدزنگ 316L؛ —. کاربرد معمول: ساخت غیر API (مثلاً پمپ بشکه‌ای پرتابل). (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on B32: فولاد ضدزنگ 316L
Note on C32: فولاد ضدزنگ 316L
Note on D32: —
Note on E32: ساخت غیر API (مثلاً پمپ بشکه‌ای پرتابل)
Note on A33: کلاس متریال در منبع ذکر نشده است.
Note on B33: —
Note on C33: —
Note on D33: —
Note on E33: در منبع ذکر نشده
Note on A36: ۳) انواع پمپ طبق API 610
Note on A37: کد نوع پمپ: OH = پروانه آویزان (Overhung)، BB = بین دو یاتاقان (Between Bearings)، VS = عمودی آویزان (Vertically Suspended)
Note on B37: نام نوع
Note on C37: شرح و کاربرد معمول
Note on A38: OH1 – Overhung, foot-mounted: یک‌مرحله‌ای، پروانه آویزان (Overhung)، پایه‌دار زیر بدنه؛ برای دما و فشار متوسط
Note on B38: یک‌مرحله‌ای، پروانه آویزان (Overhung)، پایه‌دار زیر بدنه؛ برای دما و فشار متوسط
Note on C38: یک‌مرحله‌ای، پروانه آویزان (Overhung)، پایه‌دار زیر بدنه؛ برای دما و فشار متوسط
Note on A39: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on B39: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on C39: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on A40: OH3 – Vertical in-line, separate bearing bracket: عمودی خطی (In-line) با یاتاقان مستقل از موتور
Note on B40: عمودی خطی (In-line) با یاتاقان مستقل از موتور
Note on C40: عمودی خطی (In-line) با یاتاقان مستقل از موتور
Note on A41: OH4 – Vertical in-line, rigidly coupled: عمودی خطی با کوپلینگ صلب
Note on B41: عمودی خطی با کوپلینگ صلب
Note on C41: عمودی خطی با کوپلینگ صلب
Note on A42: OH5 – Vertical in-line, close-coupled: عمودی خطی، پروانه مستقیم روی شفت موتور
Note on B42: عمودی خطی، پروانه مستقیم روی شفت موتور
Note on C42: عمودی خطی، پروانه مستقیم روی شفت موتور
Note on A43: OH6 – High-speed integral gear: پروانه پرسرعت با گیربکس یکپارچه؛ دبی کم و هد بالا
Note on B43: پروانه پرسرعت با گیربکس یکپارچه؛ دبی کم و هد بالا
Note on C43: پروانه پرسرعت با گیربکس یکپارچه؛ دبی کم و هد بالا
Note on A44: BB1 – Between bearings, 1–2 stage, axially split: بین دو یاتاقان، یک یا دو مرحله، بدنه دوتکه افقی
Note on B44: بین دو یاتاقان، یک یا دو مرحله، بدنه دوتکه افقی
Note on C44: بین دو یاتاقان، یک یا دو مرحله، بدنه دوتکه افقی
Note on A45: BB2 – Between bearings, 1–2 stage, radially split: بین دو یاتاقان، یک یا دو مرحله، بدنه شعاعی؛ دما و فشار بالا
Note on B45: بین دو یاتاقان، یک یا دو مرحله، بدنه شعاعی؛ دما و فشار بالا
Note on C45: بین دو یاتاقان، یک یا دو مرحله، بدنه شعاعی؛ دما و فشار بالا
Note on A46: BB3 – Between bearings, multistage, axially split: چندمرحله‌ای، بدنه دوتکه افقی؛ تزریق آب و انتقال پرفشار
Note on B46: چندمرحله‌ای، بدنه دوتکه افقی؛ تزریق آب و انتقال پرفشار
Note on C46: چندمرحله‌ای، بدنه دوتکه افقی؛ تزریق آب و انتقال پرفشار
Note on A47: BB4 – Between bearings, multistage, single casing radially split: چندمرحله‌ای حلقه‌ای (Ring-section) تک‌بدنه
Note on B47: چندمرحله‌ای حلقه‌ای (Ring-section) تک‌بدنه
Note on C47: چندمرحله‌ای حلقه‌ای (Ring-section) تک‌بدنه
Note on A48: BB5 – Between bearings, multistage, double casing (barrel): چندمرحله‌ای دوبدنه (Barrel)؛ سخت‌ترین سرویس‌های پرفشار
Note on B48: چندمرحله‌ای دوبدنه (Barrel)؛ سخت‌ترین سرویس‌های پرفشار
Note on C48: چندمرحله‌ای دوبدنه (Barrel)؛ سخت‌ترین سرویس‌های پرفشار
Note on A49: VS1 – Vertically suspended, diffuser, discharge through column: عمودی آویزان در چاهک، دیفیوزری، خروجی از داخل ستون
Note on B49: عمودی آویزان در چاهک، دیفیوزری، خروجی از داخل ستون
Note on C49: عمودی آویزان در چاهک، دیفیوزری، خروجی از داخل ستون
Note on A50: VS2 – Vertically suspended, volute, discharge through column: عمودی آویزان، حلزونی، خروجی از داخل ستون
Note on B50: عمودی آویزان، حلزونی، خروجی از داخل ستون
Note on C50: عمودی آویزان، حلزونی، خروجی از داخل ستون
Note on A51: VS3 – Vertically suspended, axial flow: عمودی آویزان، جریان محوری؛ دبی زیاد و هد کم
Note on B51: عمودی آویزان، جریان محوری؛ دبی زیاد و هد کم
Note on C51: عمودی آویزان، جریان محوری؛ دبی زیاد و هد کم
Note on A52: VS4 – Vertically suspended, line-shaft, separate discharge (sump): پمپ عمودی Sump با شفت بلند و لوله خروجی جدا؛ چاهک درین و Flare KO
Note on B52: پمپ عمودی Sump با شفت بلند و لوله خروجی جدا؛ چاهک درین و Flare KO
Note on C52: پمپ عمودی Sump با شفت بلند و لوله خروجی جدا؛ چاهک درین و Flare KO
Note on A53: VS5 – Vertically suspended, cantilever sump: پمپ عمودی Sump کنسولی بدون یاتاقان غوطه‌ور
Note on B53: پمپ عمودی Sump کنسولی بدون یاتاقان غوطه‌ور
Note on C53: پمپ عمودی Sump کنسولی بدون یاتاقان غوطه‌ور
Note on A54: VS6 – Vertically suspended, double casing, diffuser (can): عمودی دوبدنه در قوطی (Can)؛ NPSH کم، مثل Off-spec و مایعات نزدیک نقطه جوش
Note on B54: عمودی دوبدنه در قوطی (Can)؛ NPSH کم، مثل Off-spec و مایعات نزدیک نقطه جوش
Note on C54: عمودی دوبدنه در قوطی (Can)؛ NPSH کم، مثل Off-spec و مایعات نزدیک نقطه جوش
Note on A55: VS7 – Vertically suspended, double casing, volute: عمودی دوبدنه حلزونی
Note on B55: عمودی دوبدنه حلزونی
Note on C55: عمودی دوبدنه حلزونی
Note on A56: OH (unspecified) – Overhung – subtype not stated: منبع فقط «Overhung» گفته و زیرنوع API را مشخص نکرده
Note on B56: منبع فقط «Overhung» گفته و زیرنوع API را مشخص نکرده
Note on C56: منبع فقط «Overhung» گفته و زیرنوع API را مشخص نکرده
Note on A57: BB (unspecified) – Between bearings – subtype not stated: منبع فقط «Between Bearings» گفته و زیرنوع API را مشخص نکرده
Note on B57: منبع فقط «Between Bearings» گفته و زیرنوع API را مشخص نکرده
Note on C57: منبع فقط «Between Bearings» گفته و زیرنوع API را مشخص نکرده
Note on A58: VS (unspecified) – Vertically suspended – subtype not stated: منبع فقط «Vertical» گفته
Note on B58: منبع فقط «Vertical» گفته
Note on C58: منبع فقط «Vertical» گفته
Note on A59: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on B59: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on C59: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on A60: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on B60: نوع پمپ در منبع ذکر نشده
Note on C60: نوع پمپ در منبع ذکر نشده
Note on A63: ۴) Incoterm – شرط تحویل قیمت‌ها و آنچه قیمت شامل می‌شود
Note on A64: کد شرط تحویل
Note on B64: معنی و تقسیم هزینه‌ها بین فروشنده و خریدار
Note on C64: ترجمه و توضیح فارسی
Note on D64: در این بانک برای کدام رکوردها به کار رفته است
Note on A65: تحویل درب کارخانه؛ همه هزینه‌های حمل، بیمه، گمرک و ترخیص با خریدار
Note on B65: تحویل درب کارخانه؛ همه هزینه‌های حمل، بیمه، گمرک و ترخیص با خریدار
Note on A66: تحویل به حمل‌کننده خریدار در محل تعیین‌شده
Note on B66: تحویل به حمل‌کننده خریدار در محل تعیین‌شده
Note on A67: تحویل روی کشتی در بندر مبدأ؛ کرایه حمل دریایی، بیمه و هزینه‌های ورود با خریدار
Note on B67: تحویل روی کشتی در بندر مبدأ؛ کرایه حمل دریایی، بیمه و هزینه‌های ورود با خریدار
Note on A68: فروشنده کرایه حمل تا بندر مقصد را می‌پردازد؛ بیمه با خریدار
Note on B68: فروشنده کرایه حمل تا بندر مقصد را می‌پردازد؛ بیمه با خریدار
Note on A69: فروشنده کرایه حمل و بیمه تا بندر مقصد را می‌پردازد
Note on B69: فروشنده کرایه حمل و بیمه تا بندر مقصد را می‌پردازد
Note on A70: تحویل در مقصد تعیین‌شده (مثلاً سایت)؛ حقوق ورودی و ترخیص با خریدار
Note on B70: تحویل در مقصد تعیین‌شده (مثلاً سایت)؛ حقوق ورودی و ترخیص با خریدار
Note on A71: تحویل در مقصد با پرداخت همه عوارض و حقوق گمرکی توسط فروشنده
Note on B71: تحویل در مقصد با پرداخت همه عوارض و حقوق گمرکی توسط فروشنده
Note on A72: خرید داخلی ریالی با تحویل در سایت
Note on B72: خرید داخلی ریالی با تحویل در سایت
Note on A73: شرط تحویل در منبع ذکر نشده است
Note on B73: شرط تحویل در منبع ذکر نشده است

## Master Database
MASTER PUMP PRICE DATABASE – v8
ستون‌های گروه‌بندی‌شده با دکمه «+» بالای ستون‌ها باز می‌شوند. سرستون زرد = ورودی Dropdown، خاکستری = فرمول. سلول زرد پررنگ = مقدار استنباطی (شاهد در Note)؛ سلول آبی = تبدیل ارز با نرخ بانک (نرخ پروژه در Note). روی هر سرستون Note توضیحی هست.
شناسایی |  |  |  |  | مشخصات کلیدی | [15 empty] | مشخصات تکمیلی |  |  | قیمت | [10 empty] | منبع و سازنده |  | دامنه کار (Scope) | [6 empty] | کنترل و ردیابی | محاسبات نرمال‌سازی و تعدیل (فرمول) | [10 empty] | کنترل و ردیابی
Row | Equipment Name | Project Name | Tag No. | Sub-Category | API 610 Type | API 610 Material Class | Capacity (m³/h) | Diff. Head (m) | Power (kW) | Size Driver kW (est.) | Standards | Pump Standard | IPS Standard | NACE MR0175 (Y/N) | Seal Type / Arrangement | API 682 Category | API 682 Seal Plan | Driver Type | Service Fluid | Quantity | Pump Family | Discharge Pressure (barg) | Power Basis | Cost Year (Jalali) | Reference Currency | Unit Price (Reference) | Unit Price EUR (source yr) | Unit Price USD (source yr) | Unit Price IRR (source yr) | Price Basis (as stated in source) | Incoterm | Escalated Unit Price EUR (target yr) | Escalated Unit Price USD (target yr) | Escalated Unit Price IRR (target yr) | Manufacturer / Supplier (as in source) | Project Phase | Scope: Driver incl. | Scope: Baseplate & Coupling | Scope: Seal Support System | Scope: Comm. Spares | Scope: 2-yr Spares | Scope: TPI | Scope: Witnessed FAT | QA Flag | MAT_F | SEAL_F | DRIVE_F | SCOPE_F | ALL_F | Normalized EUR (base config, source yr) | PPI Base | PPI Target | Floor Applies | Normalized Escalated EUR | Cost Coefficient (NormEsc EUR / kW^n) | Source Document | Remarks & Notes | Include in Totals (Y/N)
1 | 2nd Stage Separators Oil Pumps | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-CRU | Not stated | Not stated |  | 95.8 | 54.3 | 54.3 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Crude Oil | 1 | Centrifugal |  | Not stated | (Not stated) | USD | 240000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Purchase price (USD) – 18061405 pump CSV; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | 18061405_Pump_only_CSV.csv – section Pumps (row 1) | Type: Centrifugal ¦ Driver: موتور الکتریکی (E) ¦ Power: 54.3 kW ¦ Head: 95.8 m ¦ گمرک و حمل: $14400 ¦ Duplicate of the xlsx-sourced record for the same pump (see PUMPS.csv row); kept for reference, excluded from totals. ¦ Original type text: Centrifugal | N
2 | 3rd Stage Separators Oil Pumps | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-CRU | Not stated | Not stated |  | 59.9 | 33.1 | 33.1 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Crude Oil | 1 | Centrifugal |  | Not stated | (Not stated) | USD | 280000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Purchase price (USD) – 18061405 pump CSV; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | 18061405_Pump_only_CSV.csv – section Pumps (row 2) | Type: Centrifugal ¦ Driver: موتور الکتریکی (E) ¦ Power: 33.1 kW ¦ Head: 59.9 m ¦ گمرک و حمل: $16800 ¦ Duplicate of the xlsx-sourced record for the same pump (see PUMPS.csv row); kept for reference, excluded from totals. ¦ Original type text: Centrifugal | N
3 | Stabilized Oil Pump | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-CRU | Not stated | Not stated |  | 34.8 | 57.4 | 57.4 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Crude Oil | 1 | Centrifugal |  | Not stated | (Not stated) | USD | 250000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Purchase price (USD) – 18061405 pump CSV; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | 18061405_Pump_only_CSV.csv – section Pumps (row 3) | Type: Centrifugal ¦ Driver: موتور الکتریکی (E) ¦ Power: 57.4 kW ¦ Head: 34.8 m ¦ گمرک و حمل: $15000 ¦ Duplicate of the xlsx-sourced record for the same pump (see PUMPS.csv row); kept for reference, excluded from totals. ¦ Original type text: Centrifugal | N
4 | Product Oil Pump | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-CRU | Not stated | Not stated |  | 329 | 379 | 379 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Crude Oil | 1 | Centrifugal |  | Not stated | (Not stated) | USD | 420000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Purchase price (USD) – 18061405 pump CSV; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | 18061405_Pump_only_CSV.csv – section Pumps (row 4) | Type: Centrifugal ¦ Driver: موتور الکتریکی (E) ¦ Power: 379 kW ¦ Head: 329 m ¦ گمرک و حمل: $25200 ¦ Duplicate of the xlsx-sourced record for the same pump (see PUMPS.csv row); kept for reference, excluded from totals. ¦ Original type text: Centrifugal | N
5 | Off Spec Crude Pump | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-CRU | Not stated | Not stated |  | 311.3 | 48 | 48 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Crude Oil | 1 | Centrifugal |  | Not stated | (Not stated) | USD | 75000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Purchase price (USD) – 18061405 pump CSV; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | 18061405_Pump_only_CSV.csv – section Pumps (row 5) | Type: Centrifugal ¦ Driver: موتور الکتریکی (E) ¦ Power: 48 kW ¦ Head: 311.3 m ¦ گمرک و حمل: $4500 ¦ Duplicate of the xlsx-sourced record for the same pump (see PUMPS.csv row); kept for reference, excluded from totals. ¦ Original type text: Centrifugal | N
6 | Second Stage Desalter Water Criculated Pump | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-WAT | Not stated | Not stated |  | 32 | 2.2 | 2.2 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Process / Dilution Water | 1 | Centrifugal |  | Not stated | (Not stated) | USD | 60000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Purchase price (USD) – 18061405 pump CSV; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | 18061405_Pump_only_CSV.csv – section Pumps (row 6) | Type: Centrifugal ¦ Driver: موتور الکتریکی (E) ¦ Power: 2.2 kW ¦ Head: 32 m ¦ گمرک و حمل: $3600 ¦ Duplicate of the xlsx-sourced record for the same pump (see PUMPS.csv row); kept for reference, excluded from totals. ¦ Original type text: Centrifugal | N
7 | Degassing Water Pump | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-WAT | Not stated | Not stated |  | 36.2 | 13.1 | 13.1 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Process / Dilution Water | 1 | Centrifugal |  | Not stated | (Not stated) | USD | 60000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Purchase price (USD) – 18061405 pump CSV; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | 18061405_Pump_only_CSV.csv – section Pumps (row 7) | Type: Centrifugal ¦ Driver: موتور الکتریکی (E) ¦ Power: 13.1 kW ¦ Head: 36.2 m ¦ گمرک و حمل: $3600 ¦ Duplicate of the xlsx-sourced record for the same pump (see PUMPS.csv row); kept for reference, excluded from totals. ¦ Original type text: Centrifugal | N
8 | Disposal Water Pump | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-INJ | Not stated | Not stated |  | 1383 | 423 | 423 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Produced / Disposal Water | 1 | Centrifugal |  | Not stated | (Not stated) | USD | 410000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Purchase price (USD) – 18061405 pump CSV; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | 18061405_Pump_only_CSV.csv – section Pumps (row 8) | Type: Centrifugal ¦ Driver: موتور الکتریکی (E) ¦ Power: 423 kW ¦ Head: 1383 m ¦ گمرک و حمل: $24600 ¦ Duplicate of the xlsx-sourced record for the same pump (see PUMPS.csv row); kept for reference, excluded from totals. ¦ Original type text: Centrifugal | N
9 | Fresh Water Pump | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-WAT | Not stated | Not stated |  | 41 | 3.9 | 3.9 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Fresh / Potable Water | 1 | Centrifugal |  | Not stated | (Not stated) | USD | 8000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Purchase price (USD) – 18061405 pump CSV; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | 18061405_Pump_only_CSV.csv – section Pumps (row 9) | Type: Centrifugal ¦ Driver: موتور الکتریکی (E) ¦ Power: 3.9 kW ¦ Head: 41 m ¦ گمرک و حمل: $480 ¦ Duplicate of the xlsx-sourced record for the same pump (see PUMPS.csv row); kept for reference, excluded from totals. ¦ Original type text: Centrifugal | N
10 | Closed Drain Pump | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-DRN | Not stated | Not stated |  | 120 | 13.7 | 13.7 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Oily Water / Drain | 1 | Centrifugal |  | Not stated | (Not stated) | USD | 40000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Purchase price (USD) – 18061405 pump CSV; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | 18061405_Pump_only_CSV.csv – section Pumps (row 10) | Type: Centrifugal ¦ Driver: موتور الکتریکی (E) ¦ Power: 13.7 kW ¦ Head: 120 m ¦ گمرک و حمل: $2400 ¦ Duplicate of the xlsx-sourced record for the same pump (see PUMPS.csv row); kept for reference, excluded from totals. ¦ Original type text: Centrifugal | N
11 | Diesel Unlodaing pump | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-AUX | N/A (non-API 610) | Not stated |  | 27.2 | 4 | 4 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Diesel / Fuel Oil | 1 | PD-Rotary (Sliding Vane) |  | Not stated | (Not stated) | USD | 5000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Purchase price (USD) – 18061405 pump CSV; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | 18061405_Pump_only_CSV.csv – section Pumps (row 11) | Type: Sliding valve ¦ Driver: موتور الکتریکی (E) ¦ Power: 4 kW ¦ Head: 27.2 m ¦ گمرک و حمل: $300 ¦ Duplicate of the xlsx-sourced record for the same pump (see PUMPS.csv row); kept for reference, excluded from totals. ¦ Original type text: Sliding valve | N
12 | Diesel Transfer pump | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-AUX | N/A (non-API 610) | Not stated |  | 40.8 | 0.8 | 0.8 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Diesel / Fuel Oil | 1 | PD-Rotary (Screw) |  | Not stated | (Not stated) | USD | 3000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Purchase price (USD) – 18061405 pump CSV; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | 18061405_Pump_only_CSV.csv – section Pumps (row 12) | Type: Screw ¦ Driver: موتور الکتریکی (E) ¦ Power: 0.8 kW ¦ Head: 40.8 m ¦ گمرک و حمل: $180 ¦ Duplicate of the xlsx-sourced record for the same pump (see PUMPS.csv row); kept for reference, excluded from totals. ¦ Original type text: Screw | N
13 | Sludge Discharge Water Jet Pump | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-WAT | Not stated | Not stated |  | 15 | 5 | 5 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Process / Dilution Water | 1 | Centrifugal |  | Not stated | (Not stated) | USD | 3000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Purchase price (USD) – 18061405 pump CSV; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | 18061405_Pump_only_CSV.csv – section Pumps (row 13) | Type: Centrifugal ¦ Driver: موتور الکتریکی (E) ¦ Power: 5 kW ¦ Head: 15 m ¦ گمرک و حمل: $180 ¦ Duplicate of the xlsx-sourced record for the same pump (see PUMPS.csv row); kept for reference, excluded from totals. ¦ Original type text: Centrifugal | N
14 | Flare KO Drum Pumps | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-DRN | Not stated | Not stated |  | 18 | 2 | 2 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Oily Water / Drain | 1 | Centrifugal |  | Not stated | (Not stated) | USD | 40000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Purchase price (USD) – 18061405 pump CSV; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | 18061405_Pump_only_CSV.csv – section Pumps (row 14) | Type: Centrifugal ¦ Driver: موتور الکتریکی (E) ¦ Power: 2 kW ¦ Head: 18 m ¦ گمرک و حمل: $2400 ¦ Duplicate of the xlsx-sourced record for the same pump (see PUMPS.csv row); kept for reference, excluded from totals. ¦ Original type text: Centrifugal | N
15 | MAIN TRANSFER PUMPS | Gachsaran 4 | P-001-A/B | ROT-CRU | Not stated | Not stated | 500 |  | 216.3 | 216.3 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Crude Oil | 2 | Centrifugal | 15.2 | Not stated | 1402 | EUR | 385000 | 385000 | 485375 | 203857500000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | EXW | 398446.6378 | 420673.219 | 277027196944.9313 | (Gachsaran 4 Basic Design MTO) | Basic Design | Not stated | Not stated | Not stated | N | N | N | Not stated | Material missing; Seal missing; | 1 | 1 | 1 | 0.98 | 0.98 | 392857.1429 | 119.251 | 123.416 | N | 406578.2018 | 16147.6817 | File PEP-Rev 140205 Gachsaran 4.xlsx, sheet 'P.ME', cells A11:H11 (service in D, spec in E, unit price in H) | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ Power: 216.3 kW ¦ مشخصات کاتالوگی: 500m3/hr, 15.2 bar, 216.3 kw ¦ Original type text: Centrifugal (assumed) ¦ GCH4 review 1405-07: Source IRR = EUR 385,000 × 1.085 × 420,000 (P.ME H11); previous bank stored the IRR figure as 1399 IRR, which overstated EUR ≈2.6× | Y
16 | AUXILLIARY TRANSFER PUMPS | Gachsaran 4 | P-002-A/B | ROT-CRU | Not stated | Not stated | 250 |  | 108.1 | 108.1 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Crude Oil | 2 | Centrifugal | 15.2 | Not stated | 1402 | EUR | 135000 | 135000 | 170196.4286 | 71482500000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | EXW | 139715.0548 | 147508.7911 | 97139406720.9499 | (Gachsaran 4 Basic Design MTO) | Basic Design | Not stated | Not stated | Not stated | N | N | N | Not stated | Material missing; Seal missing; | 1 | 1 | 1 | 0.98 | 0.98 | 137755.102 | 119.251 | 123.416 | N | 142566.3824 | 8584.6326 | File PEP-Rev 140205 Gachsaran 4.xlsx, sheet 'P.ME', cells A12:H12 (service in D, spec in E, unit price in H) | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ Power: 108.1 kW ¦ مشخصات کاتالوگی: 250m3/hr, 15.2 bar, 108.1 kw ¦ Original type text: Centrifugal (assumed) ¦ GCH4 review 1405-07: Source IRR = EUR 135,000 × 1.085 × 420,000 (P.ME H12); previous bank stored the IRR figure as 1399 IRR, which overstated EUR ≈2.6× | Y
17 | OFF-SPEC PUMPS | Gachsaran 4 | P-003-A/B | ROT-CRU | Not stated | Not stated | 100 |  | 44.2 | 44.2 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Crude Oil | 2 | Centrifugal | 15.5 | Not stated | 1402 | EUR | 140000 | 140000 | 176500 | 74130000000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | EXW | 144889.6865 | 152972.0796 | 100737162525.4296 | (Gachsaran 4 Basic Design MTO) | Basic Design | Not stated | Not stated | Not stated | N | N | N | Not stated | Material missing; Seal missing; | 1 | 1 | 1 | 0.98 | 0.98 | 142857.1429 | 119.251 | 123.416 | N | 147846.6188 | 15225.0257 | File PEP-Rev 140205 Gachsaran 4.xlsx, sheet 'P.ME', cells A13:H13 (service in D, spec in E, unit price in H) | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ Power: 44.2 kW ¦ NACE MR0175: YES ¦ مشخصات کاتالوگی: 100 m3/hr , 15.5 bar,44.2 kw ¦ Original type text: Centrifugal (assumed) ¦ GCH4 review 1405-07: Source IRR = EUR 140,000 × 1.085 × 420,000 (P.ME H13); previous bank stored the IRR figure as 1399 IRR, which overstated EUR ≈2.6× | Y
18 | DEGASSING WATER PUMPS | Gachsaran 4 | P-005-A/B | ROT-WAT | Not stated | Not stated | 30 |  | 2.7 | 2.7 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Process / Dilution Water | 2 | Centrifugal | 3 | Not stated | 1402 | EUR | 34000 | 34000 | 42864.2857 | 18003000000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | EXW | 35187.4953 | 37150.3622 | 24464739470.4615 | (Gachsaran 4 Basic Design MTO) | Basic Design | Not stated | Not stated | Not stated | N | N | N | Not stated | Material missing; Seal missing; | 1 | 1 | 1 | 0.98 | 0.98 | 34693.8776 | 119.251 | 123.416 | N | 35905.6074 | 19785.3629 | File PEP-Rev 140205 Gachsaran 4.xlsx, sheet 'P.ME', cells A14:H14 (service in D, spec in E, unit price in H) | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ Power: 2.7 kW ¦ مشخصات کاتالوگی: 30m3/hr, 3bar, 2.7 kw ¦ Original type text: Centrifugal (assumed) ¦ GCH4 review 1405-07: Source IRR = EUR 34,000 × 1.085 × 420,000 (P.ME H14); previous bank stored the IRR figure as 1399 IRR, which overstated EUR ≈2.6× | Y
19 | DILUTION WATER PUMPS | Gachsaran 4 | P-103 | ROT-WAT | Not stated | Not stated | 40 |  | 12 | 12 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Process / Dilution Water | 1 | Centrifugal | 10.4 | Not stated | 1402 | EUR | 29000 | 29000 | 36560.7143 | 15355500000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | EXW | 30012.8636 | 31687.0736 | 20866983665.9818 | (Gachsaran 4 Basic Design MTO) | Basic Design | Not stated | Not stated | Not stated | N | N | N | Not stated | Material missing; Seal missing; | 1 | 1 | 1 | 0.98 | 0.98 | 29591.8367 | 119.251 | 123.416 | N | 30625.371 | 6895.6087 | File PEP-Rev 140205 Gachsaran 4.xlsx, sheet 'P.ME', cells A17:H17 (service in D, spec in E, unit price in H) | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ Power: 12 kW ¦ مشخصات کاتالوگی: 40m3/hr , 10.4 bar, 12 kw ¦ Original type text: Centrifugal (assumed) ¦ GCH4 review 1405-07: Source IRR = EUR 29,000 × 1.085 × 420,000 (P.ME H17); previous bank stored the IRR figure as 1399 IRR, which overstated EUR ≈2.6× | Y
20 | DILUTION WATER PUMPS | Gachsaran 4 | P-106-A1/A2 | ROT-WAT | Not stated | Not stated | 20 |  | 6 | 6 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Process / Dilution Water | 2 | Centrifugal | 10.4 | Not stated | 1402 | EUR | 27500 | 27500 | 34669.6429 | 14561250000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | EXW | 28460.4741 | 30048.0871 | 19787656924.638 | (Gachsaran 4 Basic Design MTO) | Basic Design | Not stated | Not stated | Not stated | N | N | N | Not stated | Material missing; Seal missing; | 1 | 1 | 1 | 0.98 | 0.98 | 28061.2245 | 119.251 | 123.416 | N | 29041.3001 | 9911.1787 | File PEP-Rev 140205 Gachsaran 4.xlsx, sheet 'P.ME', cells A18:H18 (service in D, spec in E, unit price in H) | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ Power: 6 kW ¦ مشخصات کاتالوگی: 20 m3/hr, 10.4 bar, 6 kw ¦ Original type text: Centrifugal (assumed) ¦ GCH4 review 1405-07: Source IRR = EUR 27,500 × 1.085 × 420,000 (P.ME H18); previous bank stored the IRR figure as 1399 IRR, which overstated EUR ≈2.6× | Y
21 | DEAERATED WATER PUMPS | Gachsaran 4 | P-102-A/B | ROT-WAT | Not stated | Not stated | 20 |  | 1.35 | 1.35 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Deaerated Water | 2 | Centrifugal | 2.4 | Not stated | 1402 | EUR | 15000 | 15000 | 18910.7143 | 7942500000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | EXW | 15523.895 | 16389.8657 | 10793267413.4389 | (Gachsaran 4 Basic Design MTO) | Basic Design | Not stated | Not stated | Not stated | N | N | N | Not stated | Material missing; Seal missing; | 1 | 1 | 1 | 0.98 | 0.98 | 15306.1224 | 119.251 | 123.416 | N | 15840.7092 | 13230.4422 | File PEP-Rev 140205 Gachsaran 4.xlsx, sheet 'P.ME', cells A20:H20 (service in D, spec in E, unit price in H) | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ Power: 1.35 kW ¦ مشخصات کاتالوگی: 20m3/hr, 2.4 bar, 1.35 kw ¦ Original type text: Centrifugal (assumed) ¦ GCH4 review 1405-07: Source IRR = EUR 15,000 × 1.085 × 420,000 (P.ME H20); previous bank stored the IRR figure as 1399 IRR, which overstated EUR ≈2.6× | Y
22 | DEAERATED WATER PUMPS | Gachsaran 4 | P-105 | ROT-WAT | Not stated | Not stated | 40 |  | 2.7 | 2.7 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Deaerated Water | 1 | Centrifugal | 2.4 | Not stated | 1402 | EUR | 17000 | 17000 | 21432.1429 | 9001500000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | EXW | 17593.7476 | 18575.1811 | 12232369735.2307 | (Gachsaran 4 Basic Design MTO) | Basic Design | Not stated | Not stated | Not stated | N | N | N | Not stated | Material missing; Seal missing; | 1 | 1 | 1 | 0.98 | 0.98 | 17346.9388 | 119.251 | 123.416 | N | 17952.8037 | 9892.6814 | File PEP-Rev 140205 Gachsaran 4.xlsx, sheet 'P.ME', cells A21:H21 (service in D, spec in E, unit price in H) | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ Power: 2.7 kW ¦ مشخصات کاتالوگی: 40m3/hr, 2.4 bar, 2.7 kw ¦ Original type text: Centrifugal (assumed) ¦ GCH4 review 1405-07: Source IRR = EUR 17,000 × 1.085 × 420,000 (P.ME H21); previous bank stored the IRR figure as 1399 IRR, which overstated EUR ≈2.6× | Y
23 | POTABLE WATER FILLING PUMP | Gachsaran 4 | P-104 | ROT-WAT | Not stated | Not stated | 20 |  | 1.4 | 1.4 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Fresh / Potable Water | 1 | Centrifugal | 2.5 | Not stated | 1402 | EUR | 11000 | 11000 | 13867.8571 | 5824500000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | EXW | 11384.1897 | 12019.2348 | 7915062769.8552 | (Gachsaran 4 Basic Design MTO) | Basic Design | Not stated | Not stated | Not stated | N | N | N | Not stated | Material missing; Seal missing; | 1 | 1 | 1 | 0.98 | 0.98 | 11224.4898 | 119.251 | 123.416 | N | 11616.5201 | 9492.907 | File PEP-Rev 140205 Gachsaran 4.xlsx, sheet 'P.ME', cells A23:H23 (service in D, spec in E, unit price in H) | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ Power: 1.4 kW ¦ مشخصات کاتالوگی: 20m3/hr, 2.5 bar, 1.4 kw ¦ Original type text: Centrifugal (assumed) ¦ GCH4 review 1405-07: Source IRR = EUR 11,000 × 1.085 × 420,000 (P.ME H23); previous bank stored the IRR figure as 1399 IRR, which overstated EUR ≈2.6× | Y
24 | WATER INJECTION MAIN PUMPS | Gachsaran 4 | P-201-A/B/C | ROT-INJ | Not stated | Not stated | 73 |  | 73.6 | 73.6 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Produced / Disposal Water | 3 | Centrifugal | 36.3 | Not stated | 1402 | EUR | 430000 | 430000 | 542107.1429 | 227685000000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | EXW | 445018.3227 | 469842.8161 | 309406999185.2479 | (Gachsaran 4 Basic Design MTO) | Basic Design | Not stated | Not stated | Not stated | N | N | N | Not stated | Material missing; Seal missing; | 1 | 1 | 1 | 0.98 | 0.98 | 438775.5102 | 119.251 | 123.416 | N | 454100.3293 | 34436.9855 | File PEP-Rev 140205 Gachsaran 4.xlsx, sheet 'P.ME', cells A24:H24 (service in D, spec in E, unit price in H) | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ Power: 73.6 kW ¦ NACE MR0175: YES ¦ مشخصات کاتالوگی: 73m3/hr (each),36.3 bar, 73.6 kw ¦ Original type text: Centrifugal (assumed) ¦ GCH4 review 1405-07: Source IRR = EUR 430,000 × 1.085 × 420,000 (P.ME H24); previous bank stored the IRR figure as 1399 IRR, which overstated EUR ≈2.6× | Y
25 | WATER INJECTION BOOSTER PUMPS | Gachsaran 4 | P-206-A/B/C | ROT-INJ | Not stated | Not stated | 36.5 |  | 36.5 | 36.5 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Produced / Disposal Water | 3 | Centrifugal | 36.3 | Not stated | 1402 | EUR | 285000 | 285000 | 359303.5714 | 150907500000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | EXW | 294954.0046 | 311407.4479 | 205072080855.3387 | (Gachsaran 4 Basic Design MTO) | Basic Design | Not stated | Not stated | Not stated | N | N | N | Not stated | Material missing; Seal missing; | 1 | 1 | 1 | 0.98 | 0.98 | 290816.3265 | 119.251 | 123.416 | N | 300973.4741 | 34765.822 | File PEP-Rev 140205 Gachsaran 4.xlsx, sheet 'P.ME', cells A25:H25 (service in D, spec in E, unit price in H) | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ Power: 36.5 kW ¦ NACE MR0175: YES ¦ مشخصات کاتالوگی: 36.5m3/hr (each),36.3 bar, 36.5 kw ¦ Original type text: Centrifugal (assumed) ¦ GCH4 review 1405-07: Source IRR = EUR 285,000 × 1.085 × 420,000 (P.ME H25); previous bank stored the IRR figure as 1399 IRR, which overstated EUR ≈2.6× | Y
26 | CHEMICAL INJECTION PORTABLE PUMPS | Gachsaran 4 | P-501-A/B/C | ROT-AUX | Not stated | Not stated |  |  | 0.45 | 0.45 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Chemical | 3 | Centrifugal | 2 | Not stated | 1402 | EUR | 9000 | 9000 | 11346.4286 | 4765500000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | EXW | 9314.337 | 9833.9194 | 6475960448.0633 | (Gachsaran 4 Basic Design MTO) | Basic Design | Not stated | Not stated | Not stated | N | N | N | Not stated | Material missing; Seal missing; | 1 | 1 | 1 | 0.98 | 0.98 | 9183.6735 | 119.251 | 123.416 | N | 9504.4255 | 15346.112 | File PEP-Rev 140205 Gachsaran 4.xlsx, sheet 'P.ME', cells A36:H36 (service in D, spec in E, unit price in H) | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ Power: 0.45 kW ¦ NACE MR0175: YES ¦ مشخصات کاتالوگی: .8m/h, 2bar, 0.45 kw ¦ Original type text: Centrifugal (assumed) ¦ GCH4 review 1405-07: Source IRR = EUR 9,000 × 1.085 × 420,000 (P.ME H36); previous bank stored the IRR figure as 1399 IRR, which overstated EUR ≈2.6× | Y
27 | FLARE K.O DRUM LIQUID PUMPS | Gachsaran 4 | P-601-A/B | ROT-DRN | Not stated | Not stated | 15 |  | 0.33 | 0.33 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Oily Water / Drain | 2 | Centrifugal | 0.8 | Not stated | 1402 | EUR | 28000 | 28000 | 35300 | 14826000000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | EXW | 28977.9373 | 30594.4159 | 20147432505.0859 | (Gachsaran 4 Basic Design MTO) | Basic Design | Not stated | Not stated | Not stated | N | N | N | Not stated | Material missing; Seal missing; | 1 | 1 | 1 | 0.98 | 0.98 | 28571.4286 | 119.251 | 123.416 | N | 29569.3238 | 57508.6309 | File PEP-Rev 140205 Gachsaran 4.xlsx, sheet 'P.ME', cells A46:H46 (service in D, spec in E, unit price in H) | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ Power: 0.33 kW ¦ مشخصات کاتالوگی: 15m3/hr, 0.8 bar, 0.33 kw ¦ Original type text: Centrifugal (assumed) ¦ GCH4 review 1405-07: Source IRR = EUR 28,000 × 1.085 × 420,000 (P.ME H46); previous bank stored the IRR figure as 1399 IRR, which overstated EUR ≈2.6× | Y
28 | HC CLOSED DRAIN TRANSFER PUMPS | Gachsaran 4 | P-701-A/B | ROT-DRN | Not stated | Not stated | 27.5 |  | 3.3 | 3.3 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Oily Water / Drain | 2 | Centrifugal | 4.3 | Not stated | 1402 | EUR | 53000 | 53000 | 66817.8571 | 28063500000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | EXW | 54851.0956 | 57910.8587 | 38136211527.484 | (Gachsaran 4 Basic Design MTO) | Basic Design | Not stated | Not stated | Not stated | N | N | N | Not stated | Material missing; Seal missing; | 1 | 1 | 1 | 0.98 | 0.98 | 54081.6327 | 119.251 | 123.416 | N | 55970.5057 | 27343.2962 | File PEP-Rev 140205 Gachsaran 4.xlsx, sheet 'P.ME', cells A50:H50 (service in D, spec in E, unit price in H) | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ Power: 3.3 kW ¦ مشخصات کاتالوگی: 27.5m3/hr, 4.3 bar, 3.3 kw ¦ Original type text: Centrifugal (assumed) ¦ GCH4 review 1405-07: Source IRR = EUR 53,000 × 1.085 × 420,000 (P.ME H50); previous bank stored the IRR figure as 1399 IRR, which overstated EUR ≈2.6× | Y
29 | HC CLOSED DRAIN DRUM SUMP PUMP | Gachsaran 4 | P-702A/B | ROT-DRN | Not stated | Not stated | 5.5 |  | 0.11 | 0.11 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Oily Water / Drain | 2 | Centrifugal | 7 | Not stated | 1402 | EUR | 53000 | 53000 | 66817.8571 | 28063500000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | EXW | 54851.0956 | 57910.8587 | 38136211527.484 | (Gachsaran 4 Basic Design MTO) | Basic Design | Not stated | Not stated | Not stated | N | N | N | Not stated | Material missing; Seal missing; | 1 | 1 | 1 | 0.98 | 0.98 | 54081.6327 | 119.251 | 123.416 | N | 55970.5057 | 210437.7355 | File PEP-Rev 140205 Gachsaran 4.xlsx, sheet 'P.ME', cells A51:H51 (service in D, spec in E, unit price in H) | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ Power: 0.11 kW ¦ مشخصات کاتالوگی: 5.5m3/hr, 7 bar. 0.11 kw ¦ Original type text: Centrifugal (assumed) ¦ GCH4 review 1405-07: Source IRR = EUR 53,000 × 1.085 × 420,000 (P.ME H51); previous bank stored the IRR figure as 1399 IRR, which overstated EUR ≈2.6× | Y
30 | CLEAN WATER PUMPS | Gachsaran 4 | P-703-A/B | ROT-WAT | Not stated | Not stated | 11 |  | 0.54 | 0.54 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Process / Dilution Water | 2 | Centrifugal | 1.8 | Not stated | 1402 | EUR | 29000 | 29000 | 36560.7143 | 15355500000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | EXW | 30012.8636 | 31687.0736 | 20866983665.9818 | (Gachsaran 4 Basic Design MTO) | Basic Design | Not stated | Not stated | Not stated | N | N | N | Not stated | Material missing; Seal missing; | 1 | 1 | 1 | 0.98 | 0.98 | 29591.8367 | 119.251 | 123.416 | N | 30625.371 | 44324.6284 | File PEP-Rev 140205 Gachsaran 4.xlsx, sheet 'P.ME', cells A53:H53 (service in D, spec in E, unit price in H) | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ Power: 0.54 kW ¦ مشخصات کاتالوگی: 11m3/hr, 1.8 bar, 0.54 kw ¦ Original type text: Centrifugal (assumed) ¦ GCH4 review 1405-07: Source IRR = EUR 29,000 × 1.085 × 420,000 (P.ME H53); previous bank stored the IRR figure as 1399 IRR, which overstated EUR ≈2.6× | Y
31 | RECOVERED WASTE OIL PUMPS | Gachsaran 4 | P-704-A/B | ROT-DRN | Not stated | Not stated | 11 |  | 0.8 | 0.8 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Slop / Dirty Oil | 2 | Centrifugal | 2.7 | Not stated | 1402 | EUR | 35000 | 35000 | 44125 | 18532500000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | EXW | 36222.4216 | 38243.0199 | 25184290631.3574 | (Gachsaran 4 Basic Design MTO) | Basic Design | Not stated | Not stated | Not stated | N | N | N | Not stated | Material missing; Seal missing; | 1 | 1 | 1 | 0.98 | 0.98 | 35714.2857 | 119.251 | 123.416 | N | 36961.6547 | 42256.8786 | File PEP-Rev 140205 Gachsaran 4.xlsx, sheet 'P.ME', cells A54:H54 (service in D, spec in E, unit price in H) | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ Power: 0.8 kW ¦ NACE MR0175: YES ¦ مشخصات کاتالوگی: 11 m3/hr, 2.7 bar, 0.8 kw ¦ Original type text: Centrifugal (assumed) ¦ GCH4 review 1405-07: Source IRR = EUR 35,000 × 1.085 × 420,000 (P.ME H54); previous bank stored the IRR figure as 1399 IRR, which overstated EUR ≈2.6× | Y
32 | OILY WATER SEPARATOR PUMP | Gachsaran 4 | P-750 | ROT-DRN | Not stated | Not stated | 1 |  | 0.02 | 0.02 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Oily Water / Drain | 1 | Centrifugal | 0.84 | Not stated | 1402 | EUR | 13350 | 13350 | 16830.5357 | 7068825000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | EXW | 13816.2665 | 14586.9805 | 9606007997.9606 | (Gachsaran 4 Basic Design MTO) | Basic Design | Not stated | Not stated | Not stated | N | N | N | Not stated | Material missing; Seal missing; | 1 | 1 | 1 | 0.98 | 0.98 | 13622.449 | 119.251 | 123.416 | N | 14098.2312 | 147416.6812 | File PEP-Rev 140205 Gachsaran 4.xlsx, sheet 'P.ME', cells A55:H55 (service in D, spec in E, unit price in H) | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ Power: 0.02 kW ¦ مشخصات کاتالوگی: 1m3/hr, 0.84 bar, 0.02kw ¦ Original type text: Centrifugal (assumed) ¦ GCH4 review 1405-07: Source IRR = EUR 13,350 × 1.085 × 420,000 (P.ME H55); previous bank stored the IRR figure as 1399 IRR, which overstated EUR ≈2.6× | Y
33 | DIRTY OIL PUMPS | Gachsaran 4 | P-705-A/B | ROT-DRN | Not stated | Not stated | 5 |  | 0.3 | 0.3 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Slop / Dirty Oil | 2 | Centrifugal | 2 | Not stated | 1402 | EUR | 31000 | 31000 | 39082.1429 | 16414500000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | EXW | 32082.7163 | 33872.3891 | 22306085987.7737 | (Gachsaran 4 Basic Design MTO) | Basic Design | Not stated | Not stated | Not stated | N | N | N | Not stated | Material missing; Seal missing; | 1 | 1 | 1 | 0.98 | 0.98 | 31632.6531 | 119.251 | 123.416 | N | 32737.4656 | 67417.447 | File PEP-Rev 140205 Gachsaran 4.xlsx, sheet 'P.ME', cells A57:H57 (service in D, spec in E, unit price in H) | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ Power: 0.3 kW ¦ NACE MR0175: YES ¦ مشخصات کاتالوگی: 5m3/hr, 2bar, 0.3 kw ¦ Original type text: Centrifugal (assumed) ¦ GCH4 review 1405-07: Source IRR = EUR 31,000 × 1.085 × 420,000 (P.ME H57); previous bank stored the IRR figure as 1399 IRR, which overstated EUR ≈2.6× | Y
34 | RECOVERED WASTE WATER PUMPS | Gachsaran 4 | P-706-A/B | ROT-INJ | Not stated | Not stated | 33 |  | 1.35 | 1.35 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Produced / Disposal Water | 2 | Centrifugal | 1.5 | Not stated | 1402 | EUR | 28000 | 28000 | 35300 | 14826000000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | EXW | 28977.9373 | 30594.4159 | 20147432505.0859 | (Gachsaran 4 Basic Design MTO) | Basic Design | Not stated | Not stated | Not stated | N | N | N | Not stated | Material missing; Seal missing; | 1 | 1 | 1 | 0.98 | 0.98 | 28571.4286 | 119.251 | 123.416 | N | 29569.3238 | 24696.8254 | File PEP-Rev 140205 Gachsaran 4.xlsx, sheet 'P.ME', cells A58:H58 (service in D, spec in E, unit price in H) | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ Power: 1.35 kW ¦ NACE MR0175: YES ¦ مشخصات کاتالوگی: 33m3/hr, 1.5 bar, 1.35 kw ¦ Original type text: Centrifugal (assumed) ¦ GCH4 review 1405-07: Source IRR = EUR 28,000 × 1.085 × 420,000 (P.ME H58); previous bank stored the IRR figure as 1399 IRR, which overstated EUR ≈2.6× | Y
35 | DIESEL OIL PUMP | Gachsaran 4 | P-801 | ROT-AUX | Not stated | Not stated | 10 |  | 0.16 | 0.16 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Diesel / Fuel Oil | 1 | Centrifugal | 0.6 | Not stated | 1402 | EUR | 13500 | 13500 | 17019.6429 | 7148250000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | EXW | 13971.5055 | 14750.8791 | 9713940672.095 | (Gachsaran 4 Basic Design MTO) | Basic Design | Not stated | Not stated | Not stated | N | N | N | Not stated | Material missing; Seal missing; | 1 | 1 | 1 | 0.98 | 0.98 | 13775.5102 | 119.251 | 123.416 | N | 14256.6382 | 42809.9914 | File PEP-Rev 140205 Gachsaran 4.xlsx, sheet 'P.ME', cells A60:H60 (service in D, spec in E, unit price in H) | Type: Centrifugal (API 610) ¦ Driver: دیزلی (Diesel Engine) ¦ Power: 0.16 kW ¦ مشخصات کاتالوگی: 10m3/hr, 0.6 bar, 0.16 kw ¦ Original type text: Centrifugal (assumed) ¦ GCH4 review 1405-07: Source IRR = EUR 13,500 × 1.085 × 420,000 (P.ME H60); previous bank stored the IRR figure as 1399 IRR, which overstated EUR ≈2.6× | Y
36 | FIRE WATER MAIN ELECTRICAL PUMP | Gachsaran 4 | P-901A/B | ROT-FIR | Not stated | Not stated | 480 |  | 133 | 133 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Fire Water | 2 | Centrifugal | 10 | Not stated | 1402 | IRR | 37500000000 | 70821.5297 | 89285.7143 | 37500000000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; IRR lump figure ¦ source label: AACE Class 2 | EXW | 73295.066 | 77383.6906 | 50959713944.4706 | (Gachsaran 4 Basic Design MTO) | Basic Design | Not stated | Not stated | Not stated | N | N | N | Not stated | Material missing; Seal missing; | 1 | 1 | 1 | 0.98 | 0.98 | 72266.8671 | 119.251 | 123.416 | N | 74790.8837 | 3976.836 | File PEP-Rev 140205 Gachsaran 4.xlsx, sheet 'P.ME', cells A61:H61 (service in D, spec in E, unit price in H) | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ Power: 133 kW ¦ مشخصات کاتالوگی: 480m3/hr, 10 barg,133kw ¦ Original type text: Centrifugal (assumed) | Y
37 | FIRE WATER MAIN DESEL PUMP | Gachsaran 4 | P902 | ROT-FIR | Not stated | Not stated | 480 |  | 133 | 133 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Diesel Engine | Fire Water | 1 | Centrifugal | 10 | Not stated | 1402 | IRR | 45000000000 | 84985.8357 | 107142.8571 | 45000000000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; IRR lump figure ¦ source label: AACE Class 2 | EXW | 87954.0792 | 92860.4288 | 61151656733.3648 | (Gachsaran 4 Basic Design MTO) | Basic Design | Not stated | Not stated | Not stated | N | N | N | Not stated | Material missing; Seal missing; | 1 | 1 | 1.35 | 0.98 | 1.323 | 64237.2152 | 119.251 | 123.416 | N | 66480.7855 | 3534.9653 | File PEP-Rev 140205 Gachsaran 4.xlsx, sheet 'P.ME', cells A62:H62 (service in D, spec in E, unit price in H) | Type: Centrifugal (API 610) ¦ Driver: دیزلی (Diesel Engine) ¦ Power: 133 kW ¦ مشخصات کاتالوگی: 480m3/hr, 10 barg,133kw ¦ Original type text: Centrifugal (assumed) | Y
38 | FIRE WATER JOCKEY PUMPS | Gachsaran 4 | P-903-A/B | ROT-FIR | Not stated | Not stated | 15 |  | 2.5 | 2.5 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Fire Water | 2 | Centrifugal | 6 | Not stated | 1402 | IRR | 2000000000 | 3777.1483 | 4761.9048 | 2000000000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; IRR lump figure ¦ source label: AACE Class 2 | EXW | 3909.0702 | 4127.1302 | 2717851410.3718 | (Gachsaran 4 Basic Design MTO) | Basic Design | Not stated | Not stated | Not stated | N | N | N | Not stated | Material missing; Seal missing; | 1 | 1 | 1 | 0.98 | 0.98 | 3854.2329 | 119.251 | 123.416 | N | 3988.8471 | 2301.8838 | File PEP-Rev 140205 Gachsaran 4.xlsx, sheet 'P.ME', cells A63:H63 (service in D, spec in E, unit price in H) | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ Power: 2.5 kW ¦ مشخصات کاتالوگی: 15m3/hr, 6 barg, 2.5 kw ¦ Original type text: Centrifugal (assumed) | Y
39 | UNIT SUPPLY WATER PUMP | Gachsaran 4 | P108A/B | ROT-WAT | Not stated | Not stated | 15 |  | 2.5 | 2.5 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Fresh / Potable Water | 2 | Centrifugal | 6 | Not stated | 1402 | EUR | 17500 | 17500 | 22062.5 | 9266250000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | EXW | 18111.2108 | 19121.51 | 12592145315.6787 | (Gachsaran 4 Basic Design MTO) | Basic Design | Not stated | Not stated | Not stated | N | N | N | Not stated | Material missing; Seal missing; | 1 | 1 | 1 | 0.98 | 0.98 | 17857.1429 | 119.251 | 123.416 | N | 18480.8274 | 10664.9152 | File PEP-Rev 140205 Gachsaran 4.xlsx, sheet 'P.ME', cells A64:H64 (service in D, spec in E, unit price in H) | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ Power: 2.5 kW ¦ مشخصات کاتالوگی: 15m3/hr, 6 barg, 2.5 kw ¦ Original type text: Centrifugal (assumed) ¦ GCH4 review 1405-07: Source IRR = EUR 17,500 × 1.085 × 420,000 (P.ME H64); previous bank stored the IRR figure as 1399 IRR, which overstated EUR ≈2.6× | Y
40 | FIRE WATER LOADING PUMP | Gachsaran 4 | P-904 | ROT-FIR | Not stated | Not stated | 30 |  | 2.5 | 2.5 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Fire Water | 1 | Centrifugal | 3 | Not stated | 1402 | EUR | 19500 | 19500 | 24583.9286 | 10325250000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | EXW | 20181.0635 | 21306.8254 | 14031247637.4705 | (Gachsaran 4 Basic Design MTO) | Basic Design | Not stated | Not stated | Not stated | N | N | N | Not stated | Material missing; Seal missing; | 1 | 1 | 1 | 0.98 | 0.98 | 19897.9592 | 119.251 | 123.416 | N | 20592.9219 | 11883.7626 | File PEP-Rev 140205 Gachsaran 4.xlsx, sheet 'P.ME', cells A68:H68 (service in D, spec in E, unit price in H) | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ Power: 2.5 kW ¦ مشخصات کاتالوگی: 30m3/hr, 3 bar, 2.5 kw ¦ Original type text: Centrifugal (assumed) ¦ GCH4 review 1405-07: Source IRR = EUR 19,500 × 1.085 × 420,000 (P.ME H68); previous bank stored the IRR figure as 1399 IRR, which overstated EUR ≈2.6× | Y
41 | Salty Crude Transfer Pumps | Koopal Asmari | P-111 A/B/C | ROT-CRU | OH2 | D-1 | 354 | 31.2 |  | 50.158 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Crude Oil | 3 | Centrifugal | 4 | Not stated | 1393 | EUR | 55000 | 55000 | 71909.4839 | 2229194000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 74308.7348 | 78453.905 | 51664485443.8569 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 1.7 | 1 | 1 | 1 | 1.7 | 32352.9412 | 91.347 | 123.416 | Y | 43711.0205 | 4172.4066 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-A (1)', cells A19:F26 + unit price EUR AK19 | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ NACE MR0175: YES ¦ وزن MTO: 6000 kg ¦ Rated Flow: 354 m³/hr ¦ Differential Head: 31.2 m ¦ Discharge Pressure: 4 Barg ¦ Material Class: D1 (Acc. to API 610) ¦ Design Code: API 610 & IPS-G-PM-105 ¦ Unit Price: EUR 55,000 (Source: 91215-KPL-ME-RE-476 R03, sheet PUMPS-A(1), tag P-111 A/B/C) ¦ Original type text: Centrifugal (OH2) ¦ Original material text: D1 – Duplex stainless steel casing & trim (API 610) ¦ KPL-A review 1405-07: Design code: API 610 & IPS-G-PM-105; installation weight 6,000 kg for tag group (INS-PUMP-A (1) AF21) | Y
42 | Salty Crude Booster Pumps | Koopal Asmari | P-114 A/B/C | ROT-CRU | OH2 | D-1 | 255 | 170 |  | 196.8665 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Crude Oil | 3 | Centrifugal | 17.2 | Not stated | 1393 | EUR | 60000 | 60000 | 78446.7097 | 2431848000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 81064.0744 | 85586.0782 | 56361256847.8439 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 1.7 | 1 | 1 | 1 | 1.7 | 35294.1176 | 91.347 | 123.416 | Y | 47684.7496 | 2003.9018 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-A (1)', cells A27:F34 + unit price EUR AK27 | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ NACE MR0175: YES ¦ وزن MTO: 9600 kg ¦ Rated Flow: 255 m³/hr ¦ Differential Head: 170 m ¦ Discharge Pressure: 17.2 Barg ¦ Material Class: D1 (Acc. to API 610) ¦ Design Code: API 610 & IPS-G-PM-105 ¦ Unit Price: EUR 60,000 (Source: 91215-KPL-ME-RE-476 R03, sheet PUMPS-A(1), tag P-114 A/B/C) ¦ Original type text: Centrifugal (OH2) ¦ Original material text: D1 – Duplex stainless steel casing & trim (API 610) ¦ KPL-A review 1405-07: Design code: API 610 & IPS-G-PM-105; installation weight 9,600 kg for tag group (INS-PUMP-A (1) AF23) | Y
43 | Dirty Oil Pumps | Koopal Asmari | P-135 A/B | ROT-DRN | N/A (non-API 610) | D-1 | 5 |  |  |  | API 676 + IPS-M-PM-140 | API 676 | IPS-M-PM-140 | N | Not stated | Not stated | Not stated | Electric Motor | Slop / Dirty Oil | 2 | PD-Rotary (Gear) | 5.3 | Not stated | 1393 | EUR | 10000 | 10000 | 13074.4516 | 405308000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 13510.6791 | 14264.3464 | 9393542807.974 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; Size driver missing; | 1.7 | 1 | 1 | 1 | 1.7 | 5882.3529 | 91.347 | 123.416 | N | 7947.4583 |  | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-A (1)', cells A35:F41 + unit price EUR AK35 | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ NACE MR0175: YES ¦ وزن MTO: 1000 kg ¦ Rated Flow: 5 m³/hr ¦ Discharge Pressure: 5.3 Barg ¦ Material Class: D1 (Acc. to API 610) ¦ Design Code: API 676 & IPS-M-PM-140 ¦ Unit Price: EUR 10,000 (Source: 91215-KPL-ME-RE-476 R03, sheet PUMPS-A(1), tag P-135 A/B) ¦ Original type text: P.D.-Rotary (Ext. Gear) ¦ Original material text: D1 – Duplex stainless steel casing & trim (API 610) ¦ KPL-A review 1405-07: Design code: API 676 & IPS-M-PM-140; installation weight 1,000 kg for tag group (INS-PUMP-A (1) AF25) | Y
44 | Free Water Transfer Pumps | Koopal Asmari | P-136 A/B | ROT-WAT | OH2 | D-2 | 21 | 27.6 |  | 2.6322 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Process / Dilution Water | 2 | Centrifugal | 4 | Not stated | 1393 | EUR | 30000 | 30000 | 39223.3548 | 1215924000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 40532.0372 | 42793.0391 | 28180628423.922 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 1.9 | 1 | 1 | 1 | 1.9 | 15789.4737 | 91.347 | 123.416 | Y | 21332.6511 | 11935.9831 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-A (1)', cells A42:F49 + unit price EUR AK42 | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ وزن MTO: 1200 kg ¦ Rated Flow: 21 m³/hr ¦ Differential Head: 27.6 m ¦ Discharge Pressure: 4 Barg ¦ Material Class: D2 (Acc. to API 610) ¦ Design Code: API 610 & IPS-G-PM-105 ¦ Unit Price: EUR 30,000 (Source: 91215-KPL-ME-RE-476 R03, sheet PUMPS-A(1), tag P-136 A/B) ¦ Original type text: Centrifugal (OH2) ¦ Original material text: D2 – Super-duplex stainless steel casing & trim (API 610) ¦ KPL-A review 1405-07: Design code: API 610 & IPS-G-PM-105; installation weight 1,200 kg for tag group (INS-PUMP-A (1) AF27) | Y
45 | Disposal Water Injection Main Pumps | Koopal Asmari | P-137 A/B | ROT-INJ | BB3 | D-2 | 73 | 607.4 |  | 201.3633 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Produced / Disposal Water | 2 | Centrifugal | 74.4 | Not stated | 1393 | EUR | 210000 | 210000 | 274563.4839 | 8511468000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 283724.2602 | 299551.2738 | 197264398967.4538 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 1.9 | 1 | 1 | 1 | 1.9 | 110526.3158 | 91.347 | 123.416 | Y | 149328.558 | 6190.9126 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-A (2)', cells A19:F26 + unit price EUR AK19 | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ NACE MR0175: YES ¦ وزن MTO: 5000 kg ¦ Rated Flow: 73 m³/hr ¦ Differential Head: 607.4 m ¦ Discharge Pressure: 74.4 Barg ¦ Material Class: D2 (Acc. to API 610) ¦ Design Code: API 610 & IPS-G-PM-105 ¦ Unit Price: EUR 210,000 (Source: 91215-KPL-ME-RE-476 R03, sheet PUMPS-A(2), tag P-137 A/B) ¦ Original type text: Centrifugal (BB3) ¦ Original material text: D2 – Super-duplex stainless steel casing & trim (API 610) ¦ KPL-A review 1405-07: Design code: API 610 & IPS-G-PM-105; installation weight 5,000 kg for tag group (INS-PUMP-A (1) AF29) | Y
46 | Disposal Water Injection Booster Pumps | Koopal Asmari | P-139 A/B | ROT-INJ | BB3 | D-2 | 36 | 331 |  | 54.1144 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Produced / Disposal Water | 2 | Centrifugal | 37.4 | Not stated | 1393 | EUR | 150000 | 150000 | 196116.7742 | 6079620000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 202660.1859 | 213965.1955 | 140903142119.6099 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 1.9 | 1 | 1 | 1 | 1.9 | 78947.3684 | 91.347 | 123.416 | Y | 106663.2557 | 9728.0754 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-A (2)', cells A27:F34 + unit price EUR AK27 | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ NACE MR0175: YES ¦ وزن MTO: 4000 kg ¦ Rated Flow: 36 m³/hr ¦ Differential Head: 331 m ¦ Discharge Pressure: 37.4 Barg ¦ Material Class: D2 (Acc. to API 610) ¦ Design Code: API 610 & IPS-G-PM-105 ¦ Unit Price: EUR 150,000 (Source: 91215-KPL-ME-RE-476 R03, sheet PUMPS-A(2), tag P-139 A/B) ¦ Original type text: Centrifugal (BB3) ¦ Original material text: D2 – Super-duplex stainless steel casing & trim (API 610) ¦ KPL-A review 1405-07: Design code: API 610 & IPS-G-PM-105; installation weight 4,000 kg for tag group (INS-PUMP-A (1) AF31) | Y
47 | Dilution Water Pumps | Koopal Asmari | P-151 A/B | ROT-WAT | OH2 | S-5 | 23 | 158 |  | 16.5032 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Process / Dilution Water | 2 | Centrifugal | 16.7 | Not stated | 1393 | EUR | 16500 | 16500 | 21572.8452 | 668758200 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 25000 | 26394.577 | 17381700000 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 1 | 1 | 1 | 1 | 1 | 16500 | 91.347 | 123.416 | Y | 25000 | 4649.4271 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-A (2)', cells A35:F42 + unit price EUR AK35 | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ وزن MTO: 2400 kg ¦ Rated Flow: 23 m³/hr ¦ Differential Head: 158 m ¦ Discharge Pressure: 16.7 Barg ¦ Material Class: S5 (Acc. to API 610) ¦ Design Code: API 610 & IPS-G-PM-105 ¦ Unit Price: EUR 16,500 (Source: 91215-KPL-ME-RE-476 R03, sheet PUMPS-A(2), tag P-151 A/B) ¦ Original type text: Centrifugal (OH2) ¦ Original material text: S5 – Carbon steel casing & trim (API 610) ¦ KPL-A review 1405-07: Design code: API 610 & IPS-G-PM-105; installation weight 2,400 kg for tag group (INS-PUMP-A (1) AF33) | Y
48 | Dilution Water Pump | Koopal Asmari | P-152 | ROT-WAT | OH2 | S-5 | 43 | 158 |  | 30.8538 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Process / Dilution Water | 1 | Centrifugal | 16.7 | Not stated | 1393 | EUR | 17500 | 17500 | 22880.2903 | 709289000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 25000 | 26394.577 | 17381700000 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 1 | 1 | 1 | 1 | 1 | 17500 | 91.347 | 123.416 | Y | 25000 | 3194.1483 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-A (2)', cells A43:F50 + unit price EUR AK43 | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ وزن MTO: 500 kg ¦ Rated Flow: 43 m³/hr ¦ Differential Head: 158 m ¦ Discharge Pressure: 16.7 Barg ¦ Material Class: S5 (Acc. to API 610) ¦ Design Code: API 610 & IPS-G-PM-105 ¦ Unit Price: EUR 17,500 (Source: 91215-KPL-ME-RE-476 R03, sheet PUMPS-A(2), tag P-152) ¦ Original type text: Centrifugal (OH2) ¦ Original material text: S5 – Carbon steel casing & trim (API 610) ¦ KPL-A review 1405-07: Design code: API 610 & IPS-G-PM-105; installation weight 500 kg for tag group (INS-PUMP-A (1) AF35) | Y
49 | Flare K.O. Drum Pumps | Koopal Asmari | P-171 A/B | ROT-DRN | OH2 | S-6 | 15 | 50 |  | 3.406 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Oily Water / Drain | 2 | Centrifugal | 7.4 | Not stated | 1393 | EUR | 10000 | 10000 | 13074.4516 | 405308000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 25000 | 26394.577 | 17381700000 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 1.1 | 1 | 1 | 1 | 1.1 | 9090.9091 | 91.347 | 123.416 | Y | 22727.2727 | 10894.3407 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-A (3)', cells A19:F26 + unit price EUR AK19 | Type: Centrifugal (OH2) ¦ Driver: موتور الکتریکی (E) ¦ Head: 50 m ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Centrifugal (OH2) ¦ Original material text: S6 – Carbon steel casing, 12% Cr trim (API 610) ¦ KPL-A review 1405-07: Design code: API 610 & IPS-G-PM-105; installation weight 1,200 kg for tag group (INS-PUMP-A (1) AF37) | Y
50 | O.W.S. Oil Pumps | Koopal Asmari | P-231 A/B | ROT-DRN | N/A (non-API 610) | D-1 | 6 |  |  |  | API 676 + IPS-M-PM-140 | API 676 | IPS-M-PM-140 | N | Not stated | Not stated | Not stated | Electric Motor | Slop / Dirty Oil | 2 | PD-Rotary (Progressing Cavity) | 3.6 | Not stated | 1393 | EUR | 25000 | 25000 | 32686.129 | 1013270000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 33776.6976 | 35660.8659 | 23483857019.935 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; Size driver missing; | 1.7 | 1 | 1 | 1 | 1.7 | 14705.8824 | 91.347 | 123.416 | N | 19868.6457 |  | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-A (3)', cells A27:F33 + unit price EUR AK27 | Type: P.D.-Rotary (Progressing Cavity) ¦ Driver: موتور الکتریکی (E) ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: P.D.-Rotary (Progressing Cavity) ¦ Original material text: D1 – Duplex stainless steel casing & trim (API 610) ¦ KPL-A review 1405-07: Design code: API 676 & IPS-M-PM-140; installation weight 2,000 kg for tag group (INS-PUMP-A (1) AF39) | Y
51 | O.W.S. Water Pumps | Koopal Asmari | P-232 A/B | ROT-WAT | OH2 | D-2 | 11 | 27.6 |  | 1.3787 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Oily Water / Drain | 2 | Centrifugal | 3 | Not stated | 1393 | EUR | 20000 | 20000 | 26148.9032 | 810616000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 27021.3581 | 28528.6927 | 18787085615.948 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 1.9 | 1 | 1 | 1 | 1.9 | 10526.3158 | 91.347 | 123.416 | Y | 14221.7674 | 11729.0517 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-A (3)', cells A34:F41 + unit price EUR AK34 | Type: Centrifugal (OH2) ¦ Driver: موتور الکتریکی (E) ¦ Head: 27.6 m ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Centrifugal (OH2) ¦ Original material text: D2 – Super-duplex stainless steel casing & trim (API 610) ¦ KPL-A review 1405-07: Design code: API 610 & IPS-G-PM-105; installation weight 1,200 kg for tag group (INS-PUMP-A (1) AF41) | Y
52 | Closed Drain Drum Pumps | Koopal Asmari | P-234 A/B | ROT-DRN | OH2 | D-2 | 15 | 46.81 |  | 3.1887 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Oily Water / Drain | 2 | Centrifugal | 8.5 | Not stated | 1393 | EUR | 15000 | 15000 | 19611.6774 | 607962000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 25000 | 26394.577 | 17381700000 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 1.9 | 1 | 1 | 1 | 1.9 | 7894.7368 | 91.347 | 123.416 | Y | 13157.8947 | 6561.7376 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-A (3)', cells A42:F49 + unit price EUR AK42 | Type: Centrifugal (OH2) ¦ Driver: موتور الکتریکی (E) ¦ Head: 46.81 m ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Centrifugal (OH2) ¦ Original material text: D2 – Super-duplex stainless steel casing & trim (API 610) ¦ KPL-A review 1405-07: Design code: API 610 & IPS-G-PM-105; installation weight 1,400 kg for tag group (INS-PUMP-A (1) AF43) | Y
53 | Desalters Recycle Pumps | Koopal Asmari | P-113 A/B | ROT-WAT | OH2 | D-2 | 21 | 44.9 |  | 4.282 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Process / Dilution Water | 1 | Centrifugal |  | Not stated | 1393 | IRR | (Not stated) | (Not stated) | (Not stated) | (Not stated) | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); pump priced inside its package, no separate price ¦ source label: AACE Class 3 | Not stated | (PPI/FX missing) |  |  | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | No price; Seal missing; | 1.9 | 1 | 1 | 1 | 1.9 |  | 91.347 | 123.416 | Y |  |  | File 91215-KPL-ME-RE-476 R03, sheet 'DESALTERS-A', cells F31:F36 | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ وزن MTO: 1600 kg ¦ Original type text: Centrifugal (OH2) ¦ Original material text: D2 – Super-duplex stainless steel casing & trim (API 610) ¦ KPL-A review 1405-07: Priced inside Desalting Package PK-111 (DESALTERS-A AK19 = 3,500,000 EUR), no separate price; API 610 & IPS-G-PM-105; installation weight 1,600 kg (INS-PUMP-A (1) AF45) | Y
54 | IGF Water Recycle Pumps | Koopal Asmari | P-130 A/B | ROT-WAT | OH2 | D-2 |  |  |  |  | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Process / Dilution Water | 1 | Centrifugal |  | Not stated | 1393 | IRR | (Not stated) | (Not stated) | (Not stated) | (Not stated) | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); pump priced inside its package, no separate price ¦ source label: AACE Class 3 | Not stated | (PPI/FX missing) |  |  | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | No price; Seal missing; Size driver missing; | 1.9 | 1 | 1 | 1 | 1.9 |  | 91.347 | 123.416 | Y |  |  | File 91215-KPL-ME-RE-476 R03, sheet 'INS-PUMP-A (1)', cells AL47:AQ47 | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ وزن MTO: 1000 kg ¦ Original type text: Centrifugal (assumed) ¦ KPL-A review 1405-07: Priced inside IGF Package PK-131 (IWWTP-A (1) AK19 = 1,000,000 EUR), no separate price; installation weight 1,000 kg (INS-PUMP-A (1) AF47) | Y
55 | IGF De-oiled Waste Booster Pumps | Koopal Asmari | P-131 A/B | ROT-INJ | OH2 | D-2 |  |  |  |  | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Produced / Disposal Water | 1 | Centrifugal |  | Not stated | 1393 | IRR | (Not stated) | (Not stated) | (Not stated) | (Not stated) | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); pump priced inside its package, no separate price ¦ source label: AACE Class 3 | Not stated | (PPI/FX missing) |  |  | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | No price; Seal missing; Size driver missing; | 1.9 | 1 | 1 | 1 | 1.9 |  | 91.347 | 123.416 | Y |  |  | File 91215-KPL-ME-RE-476 R03, sheet 'INS-PUMP-A (1)', cells AL49:AQ49 | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ وزن MTO: 1000 kg ¦ Original type text: Centrifugal (assumed) ¦ KPL-A review 1405-07: Priced inside IGF Package PK-131 (IWWTP-A (1) AK19 = 1,000,000 EUR), no separate price; installation weight 1,000 kg (INS-PUMP-A (1) AF49) | Y
56 | IGF De-oiled Waste Booster Pumps | Koopal Asmari | P-132 A/B | ROT-INJ | OH2 | D-2 |  |  |  |  | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Produced / Disposal Water | 1 | Centrifugal |  | Not stated | 1393 | IRR | (Not stated) | (Not stated) | (Not stated) | (Not stated) | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); pump priced inside its package, no separate price ¦ source label: AACE Class 3 | Not stated | (PPI/FX missing) |  |  | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | No price; Seal missing; Size driver missing; | 1.9 | 1 | 1 | 1 | 1.9 |  | 91.347 | 123.416 | Y |  |  | File 91215-KPL-ME-RE-476 R03, sheet 'INS-PUMP-A (2)', cells AL19:AQ19 | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ وزن MTO: 1000 kg ¦ Original type text: Centrifugal (assumed) ¦ KPL-A review 1405-07: Priced inside IGF Package PK-131 (IWWTP-A (1) AK19 = 1,000,000 EUR), no separate price; installation weight 1,000 kg (INS-PUMP-A (2) AF19) | Y
57 | IGF Recovered Waste Oil Pumps | Koopal Asmari | P-133 A/B | ROT-DRN | N/A (non-API 610) | D-1 |  |  |  |  | API 676 + IPS-M-PM-140 | API 676 | IPS-M-PM-140 | N | Not stated | Not stated | Not stated | Electric Motor | Slop / Dirty Oil | 1 | PD-Rotary (Gear) |  | Not stated | 1393 | IRR | (Not stated) | (Not stated) | (Not stated) | (Not stated) | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); pump priced inside its package, no separate price ¦ source label: AACE Class 3 | Not stated | (PPI/FX missing) |  |  | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | No price; Seal missing; Size driver missing; | 1.7 | 1 | 1 | 1 | 1.7 |  | 91.347 | 123.416 | N |  |  | File 91215-KPL-ME-RE-476 R03, sheet 'INS-PUMP-A (2)', cells AL21:AQ21 | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ وزن MTO: 1000 kg ¦ Original type text: Centrifugal (assumed) ¦ KPL-A review 1405-07: Priced inside IGF Package PK-131 (IWWTP-A (1) AK19 = 1,000,000 EUR), no separate price; installation weight 1,000 kg (INS-PUMP-A (2) AF21) | Y
58 | IGF Oily Sludge Pumps | Koopal Asmari | P-134 A/B | ROT-DRN | N/A (non-API 610) | D-2 |  |  |  |  | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Sludge | 1 | PD-Rotary (Screw) |  | Not stated | 1393 | IRR | (Not stated) | (Not stated) | (Not stated) | (Not stated) | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); pump priced inside its package, no separate price ¦ source label: AACE Class 3 | Not stated | (PPI/FX missing) |  |  | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | No price; Seal missing; Size driver missing; | 1.9 | 1 | 1 | 1 | 1.9 |  | 91.347 | 123.416 | N |  |  | File 91215-KPL-ME-RE-476 R03, sheet 'INS-PUMP-A (2)', cells AL23:AQ23 | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ وزن MTO: 1400 kg ¦ Original type text: Centrifugal (assumed) ¦ KPL-A review 1405-07: Priced inside IGF Package PK-131 (IWWTP-A (1) AK19 = 1,000,000 EUR), no separate price; installation weight 1,400 kg (INS-PUMP-A (2) AF23); type corrected from "Centrifugal (assumed)" to P.D.-Rotary (Twin Screw) | Y
59 | Salty Crude Transfer Pumps | Koopal Bangestan | P-121 A/B/C | ROT-CRU | OH2 | D-1 | 186 | 33.4 |  | 28.2125 | API 610 + IPS-G-PM-105 + NACE MR0175 | API 610 | IPS-G-PM-105 | Y | Not stated | Not stated | Not stated | Electric Motor | Crude Oil | 3 | Centrifugal | 3.9 | Not stated | 1393 | EUR | 55000 | 55000 | 71909.4839 | 2229194000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 74308.7348 | 78453.905 | 51664485443.8569 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 1.7 | 1 | 1.05 | 1 | 1.785 | 30812.3249 | 91.347 | 123.416 | Y | 41629.5433 | 5612.242 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-B', cells A19:F27 + unit price EUR AK19 | Type: Centrifugal (OH2) ¦ Driver: موتور الکتریکی (E) ¦ Head: 33.4 m ¦ NACE MR0175: YES ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Centrifugal (OH2) ¦ Original material text: D1 – Duplex stainless steel casing & trim (API 610) ¦ KPL-B review 1405-07: Design code: API 610 & IPS-G-PM-105; installation weight 6,000 kg for tag group (INS-PUMP-B (1) AF21) | Y
60 | Off-Spec. Crude Pumps | Koopal Bangestan | P-122 A/B | ROT-CRU | OH2 | D-1 | 37 | 39 |  | 6.5531 | API 610 + IPS-G-PM-105 + NACE MR0175 | API 610 | IPS-G-PM-105 | Y | Not stated | Not stated | Not stated | Electric Motor | Crude Oil | 2 | Centrifugal | 5.4 | Not stated | 1393 | EUR | 15000 | 15000 | 19611.6774 | 607962000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 25000 | 26394.577 | 17381700000 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 1.7 | 1 | 1.05 | 1 | 1.785 | 8403.3613 | 91.347 | 123.416 | Y | 14005.6022 | 4533.487 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-B', cells A28:F36 + unit price EUR AK28 | Type: Centrifugal (OH2) ¦ Driver: موتور الکتریکی (E) ¦ Head: 39 m ¦ NACE MR0175: YES ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Centrifugal (OH2) ¦ Original material text: D1 – Duplex stainless steel casing & trim (API 610) ¦ KPL-B review 1405-07: Design code: API 610 & IPS-G-PM-105; installation weight 1,400 kg for tag group (INS-PUMP-B (1) AF23) | Y
61 | Salty Crude Booster Pumps | Koopal Bangestan | P-124 A/B/C | ROT-CRU | OH2 | D-1 | 173 | 186.3 |  | 146.3665 | API 610 + IPS-G-PM-105 + NACE MR0175 | API 610 | IPS-G-PM-105 | Y | Not stated | Not stated | Not stated | Electric Motor | Crude Oil | 3 | Centrifugal | 18 | Not stated | 1393 | EUR | 60000 | 60000 | 78446.7097 | 2431848000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 81064.0744 | 85586.0782 | 56361256847.8439 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 1.7 | 1 | 1.05 | 1 | 1.785 | 33613.4454 | 91.347 | 123.416 | Y | 45414.0473 | 2279.9495 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-B', cells A37:F45 + unit price EUR AK37 | Type: Centrifugal (OH2) ¦ Driver: موتور الکتریکی (E) ¦ Head: 186.3 m ¦ NACE MR0175: YES ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Centrifugal (OH2) ¦ Original material text: D1 – Duplex stainless steel casing & trim (API 610) ¦ KPL-B review 1405-07: Design code: API 610 & IPS-G-PM-105; installation weight 7,500 kg for tag group (INS-PUMP-B (1) AF25) | Y
62 | Dirty Oil Pumps | Koopal Bangestan | P-145 A/B | ROT-DRN | N/A (non-API 610) | D-1 | 5 |  |  |  | API 676 + IPS-M-PM-140 + NACE MR0175 | API 676 | IPS-M-PM-140 | Y | Not stated | Not stated | Not stated | Electric Motor | Slop / Dirty Oil | 2 | PD-Rotary (Gear) | 6.5 | Not stated | 1393 | EUR | 10000 | 10000 | 13074.4516 | 405308000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 13510.6791 | 14264.3464 | 9393542807.974 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; Size driver missing; | 1.7 | 1 | 1.05 | 1 | 1.785 | 5602.2409 | 91.347 | 123.416 | N | 7569.0079 |  | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-B (2)', cells A19:F26 + unit price EUR AK19 | Type: P.D.-Rotary (Ext. Gear) ¦ Driver: موتور الکتریکی (E) ¦ NACE MR0175: YES ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: P.D.-Rotary (Ext. Gear) ¦ Original material text: D1 – Duplex stainless steel casing & trim (API 610) ¦ KPL-B review 1405-07: Design code: API 676 & IPS-M-PM-140; installation weight 1,000 kg for tag group (INS-PUMP-B (1) AF27) | Y
63 | Free Water Transfer Pumps | Koopal Bangestan | P-146 A/B | ROT-WAT | OH2 | D-2 | 14.5 | 27.6 |  | 1.8174 | API 610 + IPS-G-PM-105 + NACE MR0175 | API 610 | IPS-G-PM-105 | Y | Not stated | Not stated | Not stated | Electric Motor | Process / Dilution Water | 2 | Centrifugal | 4 | Not stated | 1393 | EUR | 35000 | 35000 | 45760.5806 | 1418578000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 47287.3767 | 49925.2123 | 32877399827.909 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 1.9 | 1 | 1.05 | 1 | 1.995 | 17543.8596 | 91.347 | 123.416 | Y | 23702.9457 | 16562.5217 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-B (2)', cells A27:F35 + unit price EUR AK27 | Type: Centrifugal (OH2) ¦ Driver: موتور الکتریکی (E) ¦ Head: 27.6 m ¦ NACE MR0175: YES ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Centrifugal (OH2) ¦ Original material text: D2 – Super-duplex stainless steel casing & trim (API 610) ¦ KPL-B review 1405-07: Design code: API 610 & IPS-G-PM-105; installation weight 1,200 kg for tag group (INS-PUMP-B (1) AF29) | Y
64 | Disposal Water Injection Main Pumps | Koopal Bangestan | P-147 A/B | ROT-INJ | BB3 | D-2 | 44 | 670 |  | 133.8783 | API 610 + IPS-G-PM-105 + NACE MR0175 | API 610 | IPS-G-PM-105 | Y | Not stated | Not stated | Not stated | Electric Motor | Produced / Disposal Water | 2 | Centrifugal | 74.4 | Not stated | 1393 | EUR | 230000 | 230000 | 300712.3871 | 9322084000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 310745.6184 | 328079.9665 | 216051484583.4018 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 1.9 | 1 | 1.05 | 1 | 1.995 | 115288.2206 | 91.347 | 123.416 | Y | 155762.2147 | 8249.6593 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-B (2)', cells A36:F44 + unit price EUR AK36 | Type: Centrifugal (BB3) ¦ Driver: موتور الکتریکی (E) ¦ Head: 670 m ¦ NACE MR0175: YES ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Centrifugal (BB3) ¦ Original material text: D2 – Super-duplex stainless steel casing & trim (API 610) ¦ KPL-B review 1405-07: Design code: API 610 & IPS-G-PM-105; installation weight 4,600 kg for tag group (INS-PUMP-B (1) AF31) | Y
65 | Disposal Water Injection Booster Pumps | Koopal Bangestan | P-149 A/B | ROT-INJ | BB3 | D-2 | 22 | 331 |  | 33.0699 | API 610 + IPS-G-PM-105 + NACE MR0175 | API 610 | IPS-G-PM-105 | Y | Not stated | Not stated | Not stated | Electric Motor | Produced / Disposal Water | 2 | Centrifugal | 37.4 | Not stated | 1393 | EUR | 160000 | 160000 | 209191.2258 | 6484928000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 216170.8649 | 228229.5419 | 150296684927.5838 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 1.9 | 1 | 1.05 | 1 | 1.995 | 80200.5013 | 91.347 | 123.416 | Y | 108356.3233 | 13279.8829 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-B (3)', cells A19:F27 + unit price EUR AK19 | Type: Centrifugal (BB3) ¦ Driver: موتور الکتریکی (E) ¦ Head: 331 m ¦ NACE MR0175: YES ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Centrifugal (BB3) ¦ Original material text: D2 – Super-duplex stainless steel casing & trim (API 610) ¦ KPL-B review 1405-07: Design code: API 610 & IPS-G-PM-105; installation weight 3,600 kg for tag group (INS-PUMP-B (1) AF33) | Y
66 | Dilution Water Pumps | Koopal Bangestan | P-161 A/B | ROT-WAT | OH2 | S-5 | 19 | 168 |  | 14.4959 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Process / Dilution Water | 2 | Centrifugal | 17.8 | Not stated | 1393 | EUR | 16500 | 16500 | 21572.8452 | 668758200 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 25000 | 26394.577 | 17381700000 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 1 | 1 | 1 | 1 | 1 | 16500 | 91.347 | 123.416 | Y | 25000 | 5025.655 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-B (3)', cells A28:F35 + unit price EUR AK28 | Type: Centrifugal (OH2) ¦ Driver: موتور الکتریکی (E) ¦ Head: 168 m ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Centrifugal (OH2) ¦ Original material text: S5 – Carbon steel casing & trim (API 610) ¦ KPL-B review 1405-07: Design code: API 610 & IPS-G-PM-105; installation weight 2,200 kg for tag group (INS-PUMP-B (1) AF35) | Y
67 | Dilution Water Pump | Koopal Bangestan | P-162 | ROT-WAT | OH2 | S-5 | 33 | 168 |  | 25.1771 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Process / Dilution Water | 1 | Centrifugal | 17.8 | Not stated | 1393 | EUR | 17500 | 17500 | 22880.2903 | 709289000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 25000 | 26394.577 | 17381700000 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 1 | 1 | 1 | 1 | 1 | 17500 | 91.347 | 123.416 | Y | 25000 | 3608.5811 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-B (3)', cells A36:F43 + unit price EUR AK36 | Type: Centrifugal (OH2) ¦ Driver: موتور الکتریکی (E) ¦ Head: 168 m ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Centrifugal (OH2) ¦ Original material text: S5 – Carbon steel casing & trim (API 610) ¦ KPL-B review 1405-07: Design code: API 610 & IPS-G-PM-105; installation weight 500 kg for tag group (INS-PUMP-B (1) AF37) | Y
68 | Flare K.O. Drum Pumps | Koopal Bangestan | P-181 A/B | ROT-DRN | OH2 | S-6 | 15 | 52 |  | 3.5422 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Oily Water / Drain | 2 | Centrifugal | 7.3 | Not stated | 1393 | EUR | 10000 | 10000 | 13074.4516 | 405308000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 25000 | 26394.577 | 17381700000 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 1.1 | 1 | 1 | 1 | 1.1 | 9090.9091 | 91.347 | 123.416 | Y | 22727.2727 | 10640.9634 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-B (4)', cells A19:F26 + unit price EUR AK19 | Type: Centrifugal (OH2) ¦ Driver: موتور الکتریکی (E) ¦ Head: 52 m ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Centrifugal (OH2) ¦ Original material text: S6 – Carbon steel casing, 12% Cr trim (API 610) ¦ KPL-B review 1405-07: Design code: API 610 & IPS-G-PM-105; installation weight 1,200 kg for tag group (INS-PUMP-B (1) AF39) ¦ KPL-B review 1405-07: NACE=N inferred by omission – VERIFY (flare KO liquid of sour Bangestan train) | Y
69 | O.W.S. Oil Pumps | Koopal Bangestan | P-241 A/B | ROT-DRN | N/A (non-API 610) | D-1 | 5.5 |  |  |  | API 676 + IPS-M-PM-140 + NACE MR0175 | API 676 | IPS-M-PM-140 | Y | Not stated | Not stated | Not stated | Electric Motor | Slop / Dirty Oil | 2 | PD-Rotary (Progressing Cavity) | 3.6 | Not stated | 1393 | EUR | 25000 | 25000 | 32686.129 | 1013270000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 33776.6976 | 35660.8659 | 23483857019.935 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; Size driver missing; | 1.7 | 1 | 1.05 | 1 | 1.785 | 14005.6022 | 91.347 | 123.416 | N | 18922.5197 |  | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-B (4)', cells A27:F34 + unit price EUR AK27 | Type: P.D.-Rotary (Progressing Cavity) ¦ Driver: موتور الکتریکی (E) ¦ NACE MR0175: YES ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: P.D.-Rotary (Progressing Cavity) ¦ Original material text: D1 – Duplex stainless steel casing & trim (API 610) ¦ KPL-B review 1405-07: Design code: API 676 & IPS-M-PM-140; installation weight 2,000 kg for tag group (INS-PUMP-B (1) AF41) | Y
70 | O.W.S. Water Pumps | Koopal Bangestan | P-242 A/B | ROT-WAT | OH2 | D-2 | 11 | 28 |  | 1.3987 | API 610 + IPS-G-PM-105 + NACE MR0175 | API 610 | IPS-G-PM-105 | Y | Not stated | Not stated | Not stated | Electric Motor | Oily Water / Drain | 2 | Centrifugal | 3 | Not stated | 1393 | EUR | 20000 | 20000 | 26148.9032 | 810616000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 27021.3581 | 28528.6927 | 18787085615.948 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 1.9 | 1 | 1.05 | 1 | 1.995 | 10025.0627 | 91.347 | 123.416 | Y | 13544.5404 | 11074.5027 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-B (4)', cells A35:F43 + unit price EUR AK35 | Type: Centrifugal (OH2) ¦ Driver: موتور الکتریکی (E) ¦ Head: 28 m ¦ NACE MR0175: YES ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Centrifugal (OH2) ¦ Original material text: D2 – Super-duplex stainless steel casing & trim (API 610) ¦ KPL-B review 1405-07: Design code: API 610 & IPS-G-PM-105; installation weight 1,200 kg for tag group (INS-PUMP-B (1) AF43) | Y
71 | Closed Drain Drum Pumps | Koopal Bangestan | P-244 A/B | ROT-DRN | OH2 | D-2 | 15 | 61 |  | 4.1553 | API 610 + IPS-G-PM-105 + NACE MR0175 | API 610 | IPS-G-PM-105 | Y | Not stated | Not stated | Not stated | Electric Motor | Oily Water / Drain | 2 | Centrifugal | 9 | Not stated | 1393 | EUR | 17500 | 17500 | 22880.2903 | 709289000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 25000 | 26394.577 | 17381700000 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 1.9 | 1 | 1.05 | 1 | 1.995 | 8771.9298 | 91.347 | 123.416 | Y | 12531.3283 | 5331.3211 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-B (5)', cells A19:F27 + unit price EUR AK19 | Type: Centrifugal (OH2) ¦ Driver: موتور الکتریکی (E) ¦ Head: 61 m ¦ NACE MR0175: YES ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Centrifugal (OH2) ¦ Original material text: D2 – Super-duplex stainless steel casing & trim (API 610) ¦ KPL-B review 1405-07: Design code: API 610 & IPS-G-PM-105; installation weight 1,400 kg for tag group (INS-PUMP-B (1) AF45) | Y
72 | Desalters Recycle Pumps | Koopal Bangestan | P-123 A/B | ROT-WAT | OH2 | D-2 | 15 | 44.9 |  | 3.0586 | API 610 + IPS-G-PM-105 + NACE MR0175 | API 610 | IPS-G-PM-105 | Y | Not stated | Not stated | Not stated | Electric Motor | Process / Dilution Water | 1 | Centrifugal |  | Not stated | 1393 | IRR | (Not stated) | (Not stated) | (Not stated) | (Not stated) | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); pump priced inside its package, no separate price ¦ source label: AACE Class 3 | Not stated | (PPI/FX missing) |  |  | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | No price; Seal missing; | 1.9 | 1 | 1.05 | 1 | 1.995 |  | 91.347 | 123.416 | Y |  |  | File 91215-KPL-ME-RE-476 R03, sheet 'DESALTERS-B', cells F32:F37 | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ وزن MTO: 1600 kg ¦ Original type text: Centrifugal (OH2) ¦ Original material text: D2 – Super-duplex stainless steel casing & trim (API 610) ¦ KPL-B review 1405-07: Priced inside Desalting Package PK-121 (DESALTERS-B AK19), no separate price; API 610 & IPS-G-PM-105; installation weight 1,600 kg (INS-PUMP-B (1) AF47) | Y
73 | IGF Water Recycle Pumps | Koopal Bangestan | P-140 A/B | ROT-WAT | OH2 | D-2 |  |  |  |  | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Process / Dilution Water | 1 | Centrifugal |  | Not stated | 1393 | IRR | (Not stated) | (Not stated) | (Not stated) | (Not stated) | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); pump priced inside its package, no separate price ¦ source label: AACE Class 3 | Not stated | (PPI/FX missing) |  |  | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | No price; Seal missing; Size driver missing; | 1.9 | 1 | 1 | 1 | 1.9 |  | 91.347 | 123.416 | Y |  |  | File 91215-KPL-ME-RE-476 R03, sheet 'INS-PUMP-B (1)', cells AL49:AQ49 | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ وزن MTO: 1000 kg ¦ Original type text: Centrifugal (assumed) ¦ KPL-B review 1405-07: Priced inside IGF Package PK-141 (IWWTP-B (1) AK19 = 600,000 EUR), no separate price; installation weight 1,000 kg (INS-PUMP-B (1) AF49) | Y
74 | IGF De-oiled Waste Booster Pumps | Koopal Bangestan | P-141 A/B | ROT-INJ | OH2 | D-2 |  |  |  |  | API 610 + IPS-G-PM-105 + NACE MR0175 | API 610 | IPS-G-PM-105 | Y | Not stated | Not stated | Not stated | Electric Motor | Produced / Disposal Water | 1 | Centrifugal |  | Not stated | 1393 | IRR | (Not stated) | (Not stated) | (Not stated) | (Not stated) | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); pump priced inside its package, no separate price ¦ source label: AACE Class 3 | Not stated | (PPI/FX missing) |  |  | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | No price; Seal missing; Size driver missing; | 1.9 | 1 | 1.05 | 1 | 1.995 |  | 91.347 | 123.416 | Y |  |  | File 91215-KPL-ME-RE-476 R03, sheet 'INS-PUMP-B (2)', cells AL19:AQ19 | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ وزن MTO: 1000 kg ¦ Original type text: Centrifugal (assumed) ¦ KPL-B review 1405-07: Priced inside IGF Package PK-141 (IWWTP-B (1) AK19 = 600,000 EUR), no separate price; installation weight 1,000 kg (INS-PUMP-B (2) AF19) | Y
75 | IGF De-oiled Waste Booster Pumps | Koopal Bangestan | P-142 A/B | ROT-INJ | OH2 | D-2 |  |  |  |  | API 610 + IPS-G-PM-105 + NACE MR0175 | API 610 | IPS-G-PM-105 | Y | Not stated | Not stated | Not stated | Electric Motor | Produced / Disposal Water | 1 | Centrifugal |  | Not stated | 1393 | IRR | (Not stated) | (Not stated) | (Not stated) | (Not stated) | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); pump priced inside its package, no separate price ¦ source label: AACE Class 3 | Not stated | (PPI/FX missing) |  |  | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | No price; Seal missing; Size driver missing; | 1.9 | 1 | 1.05 | 1 | 1.995 |  | 91.347 | 123.416 | Y |  |  | File 91215-KPL-ME-RE-476 R03, sheet 'INS-PUMP-B (2)', cells AL21:AQ21 | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ وزن MTO: 1000 kg ¦ Original type text: Centrifugal (assumed) ¦ KPL-B review 1405-07: Priced inside IGF Package PK-141 (IWWTP-B (1) AK19 = 600,000 EUR), no separate price; installation weight 1,000 kg (INS-PUMP-B (2) AF21) | Y
76 | IGF Recovered Waste Oil Pumps | Koopal Bangestan | P-143 A/B | ROT-DRN | N/A (non-API 610) | D-1 |  |  |  |  | API 676 + IPS-M-PM-140 | API 676 | IPS-M-PM-140 | N | Not stated | Not stated | Not stated | Electric Motor | Slop / Dirty Oil | 1 | PD-Rotary (Gear) |  | Not stated | 1393 | IRR | (Not stated) | (Not stated) | (Not stated) | (Not stated) | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); pump priced inside its package, no separate price ¦ source label: AACE Class 3 | Not stated | (PPI/FX missing) |  |  | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | No price; Seal missing; Size driver missing; | 1.7 | 1 | 1 | 1 | 1.7 |  | 91.347 | 123.416 | N |  |  | File 91215-KPL-ME-RE-476 R03, sheet 'INS-PUMP-B (2)', cells AL23:AQ23 | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ وزن MTO: 1000 kg ¦ Original type text: Centrifugal (assumed) ¦ KPL-B review 1405-07: Priced inside IGF Package PK-141 (IWWTP-B (1) AK19 = 600,000 EUR), no separate price; installation weight 1,000 kg (INS-PUMP-B (2) AF23) | Y
77 | IGF Oily Sludge Pumps | Koopal Bangestan | P-144 A/B | ROT-DRN | N/A (non-API 610) | D-2 |  |  |  |  | API 610 + IPS-G-PM-105 + NACE MR0175 | API 610 | IPS-G-PM-105 | Y | Not stated | Not stated | Not stated | Electric Motor | Sludge | 1 | PD-Rotary (Screw) |  | Not stated | 1393 | IRR | (Not stated) | (Not stated) | (Not stated) | (Not stated) | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); pump priced inside its package, no separate price ¦ source label: AACE Class 3 | Not stated | (PPI/FX missing) |  |  | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | No price; Seal missing; Size driver missing; | 1.9 | 1 | 1.05 | 1 | 1.995 |  | 91.347 | 123.416 | N |  |  | File 91215-KPL-ME-RE-476 R03, sheet 'INS-PUMP-B (2)', cells AL25:AQ25 | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ وزن MTO: 1400 kg ¦ Original type text: Centrifugal (assumed) ¦ KPL-B review 1405-07: Priced inside IGF Package PK-141 (IWWTP-B (1) AK19 = 600,000 EUR), no separate price; installation weight 1,400 kg (INS-PUMP-B (2) AF25); type corrected from "Centrifugal (assumed)" to P.D.-Rotary (Twin Screw) | Y
78 | Stripped Waste Water Pumps | Koopal Bangestan | P-148 A/B/C | ROT-INJ | OH2 | D-2 | 50 | 30.6 |  | 6.9482 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Produced / Disposal Water | 1 | Centrifugal |  | Not stated | 1393 | IRR | (Not stated) | (Not stated) | (Not stated) | (Not stated) | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); pump priced inside its package, no separate price ¦ source label: AACE Class 3 | Not stated | (PPI/FX missing) |  |  | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | No price; Seal missing; | 1.9 | 1 | 1 | 1 | 1.9 |  | 91.347 | 123.416 | Y |  |  | File 91215-KPL-ME-RE-476 R03, sheet 'STRIPPER-B', cells F35:F40 | Type: Centrifugal (API 610) ¦ Driver: موتور الکتریکی (E) ¦ وزن MTO: 2400 kg ¦ Original type text: Centrifugal (OH2) ¦ Original material text: D2 – Super-duplex stainless steel casing & trim (API 610) ¦ KPL-B review 1405-07: Priced inside Stripping Package PK-143 (STRIPPER-B U19), no separate price; API 610 & IPS-G-PM-105; installation weight 2,400 kg (INS-PUMP-B (2) AF27) | Y
79 | Deaerated Water Pumps | Koopal Asmari | P-153 A/B | ROT-WAT | N/A (non-API 610) | I-2 | 48 | 36 |  | 7.8474 | ISO 5199 + IPS-M-PM-115 | ISO 5199 | IPS-M-PM-115 | N | Not stated | Not stated | Not stated | Electric Motor | Deaerated Water | 2 | Centrifugal | 3 | Not stated | 1393 | EUR | 6500 | 6500 | 8498.3935 | 263450200 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 8781.9414 | 9271.8251 | 6105802825.1831 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 0.8 | 1 | 1 | 1 | 0.8 | 8125 | 91.347 | 123.416 | N | 10977.4267 | 3189.0747 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-C', cells A19:F26 + unit price EUR AK19 | Type: Centrifugal (Horizontal) ¦ Driver: موتور الکتریکی (E) ¦ Head: 36 m ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Centrifugal (Horizontal) ¦ Original material text: I2 – Cast iron casing, bronze trim (API 610) ¦ KPL-A review 1405-07: Design code: ISO 5199 & IPS-M-PM-115; installation weight 1,300 kg for tag group (INS-PUMP-C AF21) | Y
80 | Potable Water Loading Pumps | Koopal Asmari | P-158 | ROT-WAT | N/A (non-API 610) | I-2 | 33 | 31 |  | 4.6458 | ISO 5199 + IPS-M-PM-115 | ISO 5199 | IPS-M-PM-115 | N | Not stated | Not stated | Not stated | Electric Motor | Fresh / Potable Water | 1 | Centrifugal | 2.9 | Not stated | 1393 | EUR | 6500 | 6500 | 8498.3935 | 263450200 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 8781.9414 | 9271.8251 | 6105802825.1831 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 0.8 | 1 | 1 | 1 | 0.8 | 8125 | 91.347 | 123.416 | N | 10977.4267 | 4367.8283 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-C', cells A27:F34 + unit price EUR AK27 | Type: Centrifugal (Horizontal) ¦ Driver: موتور الکتریکی (E) ¦ Head: 31 m ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Centrifugal (Horizontal) ¦ Original material text: I2 – Cast iron casing, bronze trim (API 610) ¦ KPL-A review 1405-07: Design code: ISO 5199 & IPS-M-PM-115; installation weight 1,500 kg for tag group (INS-PUMP-C AF23) | Y
81 | Flare K.O. Drums Sump Pump | Koopal Asmari | P-172 | ROT-DRN | VS4 | S-6 | 5.5 | 43 |  | 1.074 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Oily Water / Drain | 1 | Centrifugal | 3.03 | Not stated | 1393 | EUR | 10000 | 10000 | 13074.4516 | 405308000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 25000 | 26394.577 | 17381700000 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 1.1 | 1 | 1 | 1 | 1.1 | 9090.9091 | 91.347 | 123.416 | Y | 22727.2727 | 21774.0404 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-C', cells A35:F42 + unit price EUR AK35 | Type: Centrifugal (VS4) ¦ Driver: موتور الکتریکی (E) ¦ Head: 43 m ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Centrifugal (VS4) ¦ Original material text: S6 – Carbon steel casing, 12% Cr trim (API 610) ¦ KPL-A review 1405-07: Design code: API 610 & IPS-G-PM-105; installation weight 300 kg for tag group (INS-PUMP-C AF25) | Y
82 | Fuel Oil Pump | Koopal Asmari | P-201 | ROT-AUX | N/A (non-API 610) | S-1 | 10 | 41 |  | 1.8619 | ISO 5199 + IPS-M-PM-115 | ISO 5199 | IPS-M-PM-115 | N | Not stated | Not stated | Not stated | Electric Motor | Diesel / Fuel Oil | 1 | Centrifugal | 3.1 | Not stated | 1393 | EUR | 7000 | 7000 | 9152.1161 | 283715600 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 9457.4753 | 9985.0425 | 6575479965.5818 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 0.9 | 1 | 1 | 1 | 0.9 | 7777.7778 | 91.347 | 123.416 | N | 10508.3059 | 7236.9035 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-C', cells A43:F50 + unit price EUR AK43 | Type: Centrifugal (Horizontal) ¦ Driver: موتور الکتریکی (E) ¦ Head: 41 m ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Centrifugal (Horizontal) ¦ Original material text: S1 – Carbon steel casing, cast iron trim (API 610) ¦ KPL-A review 1405-07: Design code: ISO 5199 & IPS-M-PM-115; installation weight 500 kg for tag group (INS-PUMP-C AF27) | Y
83 | Closed Drain Drums Sump Pump | Koopal Asmari | P-235 | ROT-DRN | VS4 | S-6 | 5.5 | 31 |  | 0.7743 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Oily Water / Drain | 1 | Centrifugal | 3.4 | Not stated | 1393 | EUR | 10000 | 10000 | 13074.4516 | 405308000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 25000 | 26394.577 | 17381700000 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 1.1 | 1 | 1 | 1 | 1.1 | 9090.9091 | 91.347 | 123.416 | Y | 22727.2727 | 26497.389 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-C (2)', cells A19:F26 + unit price EUR AK19 | Type: Centrifugal (VS4) ¦ Driver: موتور الکتریکی (E) ¦ Head: 31 m ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Centrifugal (VS4) ¦ Original material text: S6 – Carbon steel casing, 12% Cr trim (API 610) ¦ KPL-A review 1405-07: Design code: API 610 & IPS-G-PM-105; installation weight 350 kg for tag group (INS-PUMP-C AF29) | Y
84 | Fire Water Pump-Elect. Motor Driven | Koopal Asmari | P-270 | ROT-FIR | BB (unspecified) | I-2 | 770 | 107 |  | 374.1599 | NFPA 20 + IPS-M-PM-125 | NFPA 20 | IPS-M-PM-125 | N | Not stated | Not stated | Not stated | Electric Motor | Fire Water | 1 | Centrifugal | 11.3 | Not stated | 1393 | EUR | 70000 | 70000 | 91521.1613 | 2837156000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 94574.7534 | 99850.4246 | 65754799655.8179 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 0.8 | 1 | 1 | 1 | 0.8 | 87500 | 91.347 | 123.416 | N | 118218.4418 | 3379.4881 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-C (2)', cells A27:F35 + unit price EUR AK27 | Type: Centrifugal (Horizontal, ¦ Driver: موتور الکتریکی (E) ¦ Head: 107 m ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Centrifugal (Horizontal, ¦ Original material text: I2 – Cast iron casing, bronze trim (API 610) ¦ KPL-A review 1405-07: Design code: NFPA 20 & IPS-M-PM-125; installation weight 2,500 kg for tag group (INS-PUMP-C AF31) | Y
85 | Fire Water Pump-Diesel Engine Driven | Koopal Asmari | P-271 | ROT-FIR | BB (unspecified) | I-2 | 770 | 88.7 |  | 310.168 | NFPA 20 + IPS-M-PM-125 | NFPA 20 | IPS-M-PM-125 | N | Not stated | Not stated | Not stated | Diesel Engine | Fire Water | 1 | Centrifugal | 9.5 | Not stated | 1393 | EUR | 90000 | 90000 | 117670.0645 | 3647772000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 121596.1115 | 128379.1173 | 84541885271.7659 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 0.8 | 1 | 1.35 | 1 | 1.08 | 83333.3333 | 91.347 | 123.416 | N | 112588.9922 | 3601.9503 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-C (2)', cells A36:F44 + unit price EUR AK36 | Type: Centrifugal (Horizontal, ¦ Driver: دیزلی (Diesel Engine) ¦ Head: 88.7 m ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Centrifugal (Horizontal, ¦ Original material text: I2 – Cast iron casing, bronze trim (API 610) ¦ KPL-A review 1405-07: Design code: NFPA 20 & IPS-M-PM-125; installation weight 6,000 kg for tag group (INS-PUMP-C AF33) | Y
86 | Fire Water Jockey Pumps | Koopal Asmari | P-272 A/B | ROT-FIR | OH (unspecified) | I-2 | 16.5 | 107 |  | 8.0177 | NFPA 20 + IPS-M-PM-125 | NFPA 20 | IPS-M-PM-125 | N | Not stated | Not stated | Not stated | Electric Motor | Fire Water | 2 | Centrifugal | 11.3 | Not stated | 1393 | EUR | 15000 | 15000 | 19611.6774 | 607962000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 20266.0186 | 21396.5196 | 14090314211.961 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 0.8 | 1 | 1 | 1 | 0.8 | 18750 | 91.347 | 123.416 | N | 25332.5232 | 7265.2106 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-C (3)', cells A19:F27 + unit price EUR AK19 | Type: Centrifugal ¦ Driver: موتور الکتریکی (E) ¦ Head: 107 m ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Centrifugal ¦ Original material text: I2 – Cast iron casing, bronze trim (API 610) ¦ KPL-A review 1405-07: Design code: NFPA 20 & IPS-M-PM-125; installation weight 1,400 kg for tag group (INS-PUMP-C AF35) | Y
87 | Fire Water Loading Pump | Koopal Asmari | P-273 | ROT-FIR | N/A (non-API 610) | I-2 | 33 | 30.6 |  | 4.5858 | ISO 5199 + IPS-M-PM-115 | ISO 5199 | IPS-M-PM-115 | N | Not stated | Not stated | Not stated | Electric Motor | Fire Water | 1 | Centrifugal | 2.9 | Not stated | 1393 | EUR | 6500 | 6500 | 8498.3935 | 263450200 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 8781.9414 | 9271.8251 | 6105802825.1831 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 0.8 | 1 | 1 | 1 | 0.8 | 8125 | 91.347 | 123.416 | N | 10977.4267 | 4401.9967 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-C (3)', cells A28:F35 + unit price EUR AK28 | Type: Centrifugal (Horizontal) ¦ Driver: موتور الکتریکی (E) ¦ Head: 30.6 m ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Centrifugal (Horizontal) ¦ Original material text: I2 – Cast iron casing, bronze trim (API 610) ¦ KPL-A review 1405-07: Design code: ISO 5199 & IPS-M-PM-115; installation weight 750 kg for tag group (INS-PUMP-C AF37) | Y
88 | Cooling Water (Sealing System) Recycle Pumps | Koopal Asmari | P-154 A/B | ROT-WAT | N/A (non-API 610) | I-2 | 3 | 30.6 |  | 0.41689 | ISO 5199 + IPS-M-PM-115 | ISO 5199 | IPS-M-PM-115 | N | Not stated | Not stated | Not stated | Electric Motor | Cooling / Seal Water | 2 | Centrifugal |  | Not stated | 1393 | IRR | 300000000 | 7401.7784 | 9677.4194 | 300000000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); local supplier price in IRR, before project overhead ¦ source label: AACE Class 3 | EXW | 10000.3052 | 10558.1531 | 6952892226.1396 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 0.8 | 1 | 1 | 1 | 0.8 | 9252.223 | 91.347 | 123.416 | N | 12500.3816 | 21130.4161 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-C (3)', cells A41:F49 + unit price IRR U41 | Type: Centrifugal (Horizontal) ¦ Driver: موتور الکتریکی (E) ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Centrifugal (Horizontal) ¦ Original material text: I2 – Cast iron casing, bronze trim (API 610) ¦ KPL-A review 1405-07: Design code: ISO 5199 & IPS-M-PM-115; installation weight 1,000 kg for tag group (INS-PUMP-C AF39) ¦ KPL-A review 1405-07: Currency corrected EUR → IRR (PUMPS-C (3) U41) | Y
89 | Water Liquid Return Pumps (Deaeration System) | Koopal Asmari | P-157 A/B | ROT-WAT | N/A (non-API 610) | I-2 | 2 | 30.6 |  | 0.27793 | ISO 5199 + IPS-M-PM-115 | ISO 5199 | IPS-M-PM-115 | N | Not stated | Not stated | Not stated | Electric Motor | Cooling / Seal Water | 2 | Centrifugal |  | Not stated | 1393 | IRR | 250000000 | 6168.1487 | 8064.5161 | 250000000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); local supplier price in IRR, before project overhead ¦ source label: AACE Class 3 | EXW | 8333.5877 | 8798.4609 | 5794076855.1164 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 0.8 | 1 | 1 | 1 | 0.8 | 7710.1858 | 91.347 | 123.416 | N | 10416.9846 | 22458.542 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-C (4)', cells A19:F26 + unit price IRR U19 | Type: Centrifugal (Horizontal) ¦ Driver: موتور الکتریکی (E) ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Centrifugal (Horizontal) ¦ Original material text: I2 – Cast iron casing, bronze trim (API 610) ¦ KPL-A review 1405-07: Design code: ISO 5199 & IPS-M-PM-115; installation weight 1,000 kg for tag group (INS-PUMP-C AF41) ¦ KPL-A review 1405-07: Currency corrected EUR → IRR (PUMPS-C (4) U19) ¦ KPL-A review 1405-07: Source remark AW19: capacity to be confirmed & finalized by Deaerator vendor | Y
90 | Evaporation Pond Portable Pump | Koopal Asmari | P-236 | ROT-INJ | N/A (non-API 610) | D-2 | 6 | 20.4 |  | 0.55586 | JIS B 8325 | JIS B 8325 | None | N | Not stated | Not stated | Not stated | Electric Motor | Produced / Disposal Water | 1 | Centrifugal - Submersible |  | Not stated | 1393 | EUR | 20000 | 20000 | 26148.9032 | 810616000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 27021.3581 | 28528.6927 | 18787085615.948 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 1.9 | 1 | 1 | 1 | 1.9 | 10526.3158 | 91.347 | 123.416 | N | 14221.7674 | 20229.0324 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-A (4)', cells A19:F26 + unit price EUR AK19 | Type: Centrifugal , Submersible ¦ Driver: موتور الکتریکی (E) ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Centrifugal , Submersible ¦ Original material text: D2 – Super-duplex stainless steel casing & trim (API 610) ¦ KPL-A review 1405-07: Design code: JIS B 8325 ¦ KPL-A review 1405-07: IP68 (PUMPS-A (4) F22); differential pressure 2 barg ¦ Motor: Electrical motor driven, explosion proof (source) | Y
91 | Evaporation Pond Portable Pump | Koopal Bangestan | P-246 | ROT-INJ | N/A (non-API 610) | D-2 | 6 | 20.4 |  | 0.55586 | JIS B 8325 | JIS B 8325 | None | N | Not stated | Not stated | Not stated | Electric Motor | Produced / Disposal Water | 1 | Centrifugal - Submersible |  | Not stated | 1393 | EUR | 20000 | 20000 | 26148.9032 | 810616000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | FOB | 27021.3581 | 28528.6927 | 18787085615.948 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; | 1.9 | 1 | 1 | 1 | 1.9 | 10526.3158 | 91.347 | 123.416 | N | 14221.7674 | 20229.0324 | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-B (5)', cells A28:F35 + unit price EUR AK28 | Type: Centrifugal , Submersible ¦ Driver: موتور الکتریکی (E) ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Centrifugal , Submersible ¦ Original material text: D2 – Super-duplex stainless steel casing & trim (API 610) ¦ KPL-B review 1405-07: IP68 (PUMPS-B (5) F31); differential pressure 2 barg ¦ Motor: Electrical motor driven, explosion proof (source) | Y
92 | Chemical Loading Pumps | Koopal Asmari | P-220 A/B/C/D/E | ROT-AUX | N/A (non-API 610) | SS316L (non-API) | 9.6 |  |  |  | Not stated | Not stated | None | N | Not stated | Not stated | Not stated | Electric Motor | Chemical | 5 | Portable Barrel |  | Not stated | 1393 | IRR | 100000000 | 2467.2595 | 3225.8065 | 100000000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); local supplier price in IRR, before project overhead ¦ source label: AACE Class 3 | EXW | 3333.4351 | 3519.3844 | 2317630742.0465 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; Size driver missing; | 1.35 | 1 | 1 | 1 | 1.35 | 1827.5996 | 91.347 | 123.416 | N | 2469.2112 |  | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-C (3)', cells A36:F40 + unit price IRR U36 | Type: Portable Barrel Pump ¦ Driver: موتور الکتریکی (E) ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Portable Barrel Pump ¦ Original material text: S.S. 316 L – Stainless steel 316L (pump material, not an API class) ¦ KPL-A review 1405-07: Design code: (not stated) – Material S.S. 316 L ¦ KPL-A review 1405-07: Currency corrected EUR → IRR (PUMPS-C (3) U36) ¦ KPL-A review 1405-07: Flow corrected 160 m3/h → 9.6 m3/h (160 L/min) | Y
93 | Water Glycol Loading Pump | Koopal Asmari | P-116 | ROT-AUX | N/A (non-API 610) | SS316L (non-API) | 9.6 |  |  |  | Not stated | Not stated | None | N | Not stated | Not stated | Not stated | Electric Motor | Chemical | 1 | Portable Barrel |  | Not stated | 1393 | IRR | 100000000 | 2467.2595 | 3225.8065 | 100000000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); local supplier price in IRR, before project overhead ¦ source label: AACE Class 3 | EXW | 3333.4351 | 3519.3844 | 2317630742.0465 | (Koopal FEED Study / Hirgan Energy) | FEED | Not stated | Not stated | Not stated | Not stated | Not stated | N | Not stated | Seal missing; Size driver missing; | 1.35 | 1 | 1 | 1 | 1.35 | 1827.5996 | 91.347 | 123.416 | N | 2469.2112 |  | File 91215-KPL-ME-RE-476 R03, sheet 'PUMPS-C (4)', cells A27:F31 + unit price IRR U27 | Type: Portable Barrel Pump ¦ Driver: موتور الکتریکی (E) ¦ پروژه کوپال ¦ Contract 53-73-1264 ¦ Original type text: Portable Barrel Pump ¦ Original material text: S.S. 316 L – Stainless steel 316L (pump material, not an API class) ¦ KPL-A review 1405-07: Design code: (not stated) – Material S.S. 316 L ¦ KPL-A review 1405-07: Currency corrected EUR → IRR (PUMPS-C (4) U27) | Y
94 | Off Spec. Crude Pumps | Pazanan 2 | P-111 A/B | ROT-CRU | VS6 | D-1 | 45 | 139.1 |  | 28.4264 | API 610 + IPS-G-PM-105 + NACE MR0175 | API 610 | IPS-G-PM-105 | Y | Not stated | Not stated | Not stated | Electric Motor | Crude Oil | 2 | Centrifugal | 14.5 | Not stated | 1404 | EUR | 111500 | 111500 | 117719.8136 | 77522382000 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | FOB | 111500 | 117719.8136 | 77522382000 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 1.7 | 1 | 1.05 | 1 | 1.785 | 62464.986 | 123.416 | 123.416 | Y | 62464.986 | 8383.073 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', cells A8:F8 (spec in B8, price in F8) | Type: Centrifugal (VS6) ¦ Driver: موتور الکتریکی (E) ¦ Head: 139.1 m ¦ NACE MR0175: YES ¦ کد پروژه 03229 ¦ FEED Report ¦ Original type text: Centrifugal (VS6) ¦ Original material text: D1 – Duplex stainless steel casing & trim (API 610) ¦ PZN2 review 1405-07: Supply overhead ×1.18 and VAT 10% are applied on top of unit prices (PUMPS G30:H31) | Y
95 | Deaerated Water Pumps | Pazanan 2 | P-122 A/B | ROT-WAT | N/A (non-API 610) | I-2 | 53 | 35.7 |  | 8.5926 | ISO 5199 + IPS-M-PM-115 | ISO 5199 | IPS-M-PM-115 | N | Not stated | Not stated | Not stated | Electric Motor | Deaerated Water | 2 | Centrifugal | 2.9 | Not stated | 1404 | EUR | 15050 | 15050 | 15889.5354 | 10463783400 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | FOB | 15050 | 15889.5354 | 10463783400 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 0.8 | 1 | 1 | 1 | 0.8 | 18812.5 | 123.416 | 123.416 | N | 18812.5 | 5175.7161 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', cells A9:F9 (spec in B9, price in F9) | Type: Centrifugal (Horizontal) ¦ Driver: موتور الکتریکی (E) ¦ Head: 35.7 m ¦ کد پروژه 03229 ¦ FEED Report ¦ Original type text: Centrifugal (Horizontal) ¦ Original material text: I2 – Cast iron casing, bronze trim (API 610) ¦ PZN2 review 1405-07: Supply overhead ×1.18 and VAT 10% are applied on top of unit prices (PUMPS G30:H31) | Y
96 | Dilution Water Pump | Pazanan 2 | P-124 | ROT-WAT | OH2 | I-2 | 53 | 122.3 |  | 29.4364 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Process / Dilution Water | 1 | Centrifugal | 12 | Not stated | 1404 | EUR | 22250 | 22250 | 23491.1736 | 15469713000 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | FOB | 22250 | 23491.1736 | 15469713000 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 0.8 | 1 | 1 | 1 | 0.8 | 27812.5 | 123.416 | 123.416 | N | 27812.5 | 3655.1821 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', cells A10:F10 (spec in B10, price in F10) | Type: Centrifugal (OH2) ¦ Driver: موتور الکتریکی (E) ¦ Head: 122.3 m ¦ کد پروژه 03229 ¦ FEED Report ¦ Original type text: Centrifugal (OH2) ¦ Original material text: I2 – Cast iron casing, bronze trim (API 610) ¦ PZN2 review 1405-07: Supply overhead ×1.18 and VAT 10% are applied on top of unit prices (PUMPS G30:H31) | Y
97 | Dilution Water Pumps | Pazanan 2 | P-125 A/B | ROT-WAT | OH2 | I-2 | 31 | 122 |  | 17.1753 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Process / Dilution Water | 2 | Centrifugal | 13 | Not stated | 1404 | EUR | 21500 | 21500 | 22699.3363 | 14948262000 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | FOB | 21500 | 22699.3363 | 14948262000 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 0.8 | 1 | 1 | 1 | 0.8 | 26875 | 123.416 | 123.416 | N | 26875 | 4879.8441 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', cells A11:F11 (spec in B11, price in F11) | Type: Centrifugal (OH2) ¦ Driver: موتور الکتریکی (E) ¦ Head: 122 m ¦ کد پروژه 03229 ¦ FEED Report ¦ Original type text: Centrifugal (OH2) ¦ Original material text: I2 – Cast iron casing, bronze trim (API 610) ¦ PZN2 review 1405-07: Supply overhead ×1.18 and VAT 10% are applied on top of unit prices (PUMPS G30:H31) | Y
98 | Disposal Water InjectionPumps | Pazanan 2 | P-136 A/B | ROT-INJ | BB3 | D-2 | 91 | 650 |  | 268.6194 | API 610 + IPS-G-PM-105 + NACE MR0175 | API 610 | IPS-G-PM-105 | Y | Not stated | Not stated | Not stated | Electric Motor | Produced / Disposal Water | 2 | Centrifugal | 72.8 | Not stated | 1404 | EUR | 317500 | 317500 | 335211.1284 | 220747590000 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | FOB | 317500 | 335211.1284 | 220747590000 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 1.9 | 1 | 1.05 | 1 | 1.995 | 159147.8697 | 123.416 | 123.416 | Y | 159147.8697 | 5550.3244 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', cells A12:F12 (spec in B12, price in F12) | Type: Centrifugal (BB3) ¦ Driver: موتور الکتریکی (E) ¦ Head: 650 m ¦ NACE MR0175: YES ¦ کد پروژه 03229 ¦ FEED Report ¦ Original type text: Centrifugal (BB3) ¦ Original material text: D2 – Super-duplex stainless steel casing & trim (API 610) ¦ PZN2 review 1405-07: Supply overhead ×1.18 and VAT 10% are applied on top of unit prices (PUMPS G30:H31) | Y
99 | Dirty Oil Pumps | Pazanan 2 | P-137 A/B | ROT-DRN | N/A (non-API 610) | D-1 | 5 |  |  |  | API 676 + IPS-M-PM-140 + NACE MR0175 | API 676 | IPS-M-PM-140 | Y | Not stated | Not stated | Not stated | Electric Motor | Slop / Dirty Oil | 2 | PD-Rotary (Gear) | 8 | Not stated | 1404 | EUR | 30000 | 30000 | 31673.4924 | 20858040000 | Vendor inquiry 1404Q1 – average of 1 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | FOB | 30000 | 31673.4924 | 20858040000 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; Size driver missing; | 1.7 | 1 | 1.05 | 1 | 1.785 | 16806.7227 | 123.416 | 123.416 | N | 16806.7227 |  | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', cells A13:F13 (spec in B13, price in F13) | Type: P.D.-Rotary (Ext. Gear) ¦ Driver: موتور الکتریکی (E) ¦ NACE MR0175: YES ¦ کد پروژه 03229 ¦ FEED Report ¦ Original type text: P.D.-Rotary (Ext. Gear) ¦ Original material text: D1 – Duplex stainless steel casing & trim (API 610) ¦ PZN2 review 1405-07: Supply overhead ×1.18 and VAT 10% are applied on top of unit prices (PUMPS G30:H31) | Y
100 | Evaporation Pond Water Return Pumps | Pazanan 2 | P-138 A/B | ROT-INJ | OH2 | D-2 | 15 | 27 |  | 1.8392 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Produced / Disposal Water | 2 | Centrifugal | 3.2 | Not stated | 1404 | EUR | 29000 | 29000 | 30617.7094 | 20162772000 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | FOB | 29000 | 30617.7094 | 20162772000 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 1.9 | 1 | 1 | 1 | 1.9 | 15263.1579 | 123.416 | 123.416 | Y | 15263.1579 | 10589.1664 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', cells A14:F14 (spec in B14, price in F14) | Type: Centrifugal (OH2) ¦ Driver: موتور الکتریکی (E) ¦ Head: 27 m ¦ کد پروژه 03229 ¦ FEED Report ¦ Original type text: Centrifugal (OH2) ¦ Original material text: D2 – Super-duplex stainless steel casing & trim (API 610) ¦ PZN2 review 1405-07: Supply overhead ×1.18 and VAT 10% are applied on top of unit prices (PUMPS G30:H31) | Y
101 | Disposal Water InjectionPumps | Pazanan 2 | P-139 A/B/C | ROT-INJ | BB3 | D-2 | 44 | 385 |  | 76.9301 | API 610 + IPS-G-PM-105 + NACE MR0175 | API 610 | IPS-G-PM-105 | Y | Not stated | Not stated | Not stated | Electric Motor | Produced / Disposal Water | 3 | Centrifugal | 48.2 | Not stated | 1404 | EUR | 247500 | 247500 | 261306.3127 | 172078830000 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | FOB | 247500 | 261306.3127 | 172078830000 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 1.9 | 1 | 1.05 | 1 | 1.995 | 124060.1504 | 123.416 | 123.416 | Y | 124060.1504 | 9161.6701 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', cells A15:F15 (spec in B15, price in F15) | Type: Centrifugal (BB3) ¦ Driver: موتور الکتریکی (E) ¦ Head: 385 m ¦ NACE MR0175: YES ¦ کد پروژه 03229 ¦ FEED Report ¦ Original type text: Centrifugal (BB3) ¦ Original material text: D2 – Super-duplex stainless steel casing & trim (API 610) ¦ PZN2 review 1405-07: Supply overhead ×1.18 and VAT 10% are applied on top of unit prices (PUMPS G30:H31) | Y
102 | Flare K.O. Drum Pumps | Pazanan 2 | P-151 A/B | ROT-DRN | OH2 | S-6 | 10 | 40 |  | 1.8165 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Oily Water / Drain | 2 | Centrifugal | 6.8 | Not stated | 1404 | EUR | 25500 | 25500 | 26922.4686 | 17729334000 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | FOB | 25500 | 26922.4686 | 17729334000 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 1.1 | 1 | 1 | 1 | 1.1 | 23181.8182 | 123.416 | 123.416 | Y | 23181.8182 | 16203.2409 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', cells A16:F16 (spec in B16, price in F16) | Type: Centrifugal (OH2) ¦ Driver: موتور الکتریکی (E) ¦ Head: 40 m ¦ کد پروژه 03229 ¦ FEED Report ¦ Original type text: Centrifugal (OH2) ¦ Original material text: S6 – Carbon steel casing, 12% Cr trim (API 610) ¦ PZN2 review 1405-07: Supply overhead ×1.18 and VAT 10% are applied on top of unit prices (PUMPS G30:H31) | Y
103 | Closed Drain Drum Pumps | Pazanan 2 | P-161 A/B | ROT-DRN | OH2 | D-2 | 25 | 55 |  | 6.2443 | API 610 + IPS-G-PM-105 + NACE MR0175 | API 610 | IPS-G-PM-105 | Y | Not stated | Not stated | Not stated | Electric Motor | Oily Water / Drain | 2 | Centrifugal | 5 | Not stated | 1404 | EUR | 31000 | 31000 | 32729.2755 | 21553308000 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | FOB | 31000 | 32729.2755 | 21553308000 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 1.9 | 1 | 1.05 | 1 | 1.995 | 15538.8471 | 123.416 | 123.416 | Y | 15538.8471 | 5177.5889 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', cells A17:F17 (spec in B17, price in F17) | Type: Centrifugal (OH2) ¦ Driver: موتور الکتریکی (E) ¦ Head: 55 m ¦ NACE MR0175: YES ¦ کد پروژه 03229 ¦ FEED Report ¦ Original type text: Centrifugal (OH2) ¦ Original material text: D2 – Super-duplex stainless steel casing & trim (API 610) ¦ PZN2 review 1405-07: Supply overhead ×1.18 and VAT 10% are applied on top of unit prices (PUMPS G30:H31) | Y
104 | C. D. Drum / Flare K.O. Drum Sump Pump | Pazanan 2 | P-162 | ROT-DRN | VS4 | S-6 | 5 | 21.4 |  | 0.48592 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Oily Water / Drain | 1 | Centrifugal | 2 | Not stated | 1404 | EUR | 34500 | 34500 | 36424.5163 | 23986746000 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | FOB | 34500 | 36424.5163 | 23986746000 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 1.1 | 1 | 1 | 1 | 1.1 | 31363.6364 | 123.416 | 123.416 | Y | 31363.6364 | 48360.0267 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', cells A18:F18 (spec in B18, price in F18) | Type: Centrifugal (VS4) ¦ Driver: موتور الکتریکی (E) ¦ Head: 21.4 m ¦ کد پروژه 03229 ¦ FEED Report ¦ Original type text: Centrifugal (VS4) ¦ Original material text: S6 – Carbon steel casing, 12% Cr trim (API 610) ¦ PZN2 review 1405-07: Supply overhead ×1.18 and VAT 10% are applied on top of unit prices (PUMPS G30:H31) | Y
105 | O.W.S. Oil Pumps | Pazanan 2 | P-163 A/B | ROT-DRN | N/A (non-API 610) | D-1 | 5 |  |  |  | API 676 + IPS-M-PM-140 + NACE MR0175 | API 676 | IPS-M-PM-140 | Y | Not stated | Not stated | Not stated | Electric Motor | Slop / Dirty Oil | 2 | PD-Rotary (Progressing Cavity) | 6.4 | Not stated | 1393 | EUR | 25000 | 25000 | 32686.129 | 1013270000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) – no 1404 quotation received (all vendors declined) | FOB | 33776.6976 | 35660.8659 | 23483857019.935 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; Size driver missing; | 1.7 | 1 | 1.05 | 1 | 1.785 | 14005.6022 | 91.347 | 123.416 | N | 18922.5197 |  | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', cells A19:F19 (spec in B19, price in F19) | Type: P.D.-Rotary (Progressing Cavity) ¦ Driver: موتور الکتریکی (E) ¦ NACE MR0175: YES ¦ کد پروژه 03229 ¦ FEED Report ¦ Original type text: P.D.-Rotary (Progressing Cavity) ¦ Original material text: D1 – Duplex stainless steel casing & trim (API 610) ¦ PZN2 review 1405-07: Price reset to the 1393 base (25,000 EUR FOB) because 38,801.91 EUR was 25,000 × 1.552 escalation – avoids double escalation ¦ PZN2 review 1405-07: Supply overhead ×1.18 and VAT 10% are applied on top of unit prices (PUMPS G30:H31) | Y
106 | O.W.S. Water Pumps | Pazanan 2 | P-164 A/B | ROT-WAT | OH2 | D-2 | 15 | 50 |  | 3.406 | API 610 + IPS-G-PM-105 + NACE MR0175 | API 610 | IPS-G-PM-105 | Y | Not stated | Not stated | Not stated | Electric Motor | Oily Water / Drain | 2 | Centrifugal | 5.7 | Not stated | 1404 | EUR | 29600 | 29600 | 31251.1792 | 20579932800 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | FOB | 29600 | 31251.1792 | 20579932800 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 1.9 | 1 | 1.05 | 1 | 1.995 | 14837.0927 | 123.416 | 123.416 | Y | 14837.0927 | 7112.1751 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', cells A20:F20 (spec in B20, price in F20) | Type: Centrifugal (OH2) ¦ Driver: موتور الکتریکی (E) ¦ Head: 50 m ¦ NACE MR0175: YES ¦ کد پروژه 03229 ¦ FEED Report ¦ Original type text: Centrifugal (OH2) ¦ Original material text: D2 – Super-duplex stainless steel casing & trim (API 610) ¦ PZN2 review 1405-07: Supply overhead ×1.18 and VAT 10% are applied on top of unit prices (PUMPS G30:H31) | Y
107 | Oily Water Basin Pumps | Pazanan 2 | P-165 A/B | ROT-DRN | OH2 | S-6 | 15 | 20 |  | 1.3624 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Oily Water / Drain | 2 | Centrifugal | 2.5 | Not stated | 1404 | EUR | 26250 | 26250 | 27714.3059 | 18250785000 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | FOB | 26250 | 27714.3059 | 18250785000 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 1.1 | 1 | 1 | 1 | 1.1 | 23863.6364 | 123.416 | 123.416 | Y | 23863.6364 | 19822.3098 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', cells A21:F21 (spec in B21, price in F21) | Type: Centrifugal (OH2) ¦ Driver: موتور الکتریکی (E) ¦ Head: 20 m ¦ کد پروژه 03229 ¦ FEED Report ¦ Original type text: Centrifugal (OH2) ¦ Original material text: S6 – Carbon steel casing, 12% Cr trim (API 610) ¦ PZN2 review 1405-07: Supply overhead ×1.18 and VAT 10% are applied on top of unit prices (PUMPS G30:H31) | Y
108 | Fuel Oil Pump | Pazanan 2 | P-171 | ROT-AUX | N/A (non-API 610) | S-1 | 10 | 21 |  | 0.95368 | ISO 5199 + IPS-M-PM-115 | ISO 5199 | IPS-M-PM-115 | N | Not stated | Not stated | Not stated | Electric Motor | Diesel / Fuel Oil | 1 | Centrifugal | 2 | Not stated | 1404 | EUR | 21000 | 21000 | 22171.4447 | 14600628000 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | FOB | 21000 | 22171.4447 | 14600628000 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 0.9 | 1 | 1 | 1 | 0.9 | 23333.3333 | 123.416 | 123.416 | N | 23333.3333 | 24006.8731 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', cells A22:F22 (spec in B22, price in F22) | Type: Centrifugal (Horizontal) ¦ Driver: موتور الکتریکی (E) ¦ Head: 21 m ¦ کد پروژه 03229 ¦ FEED Report ¦ Original type text: Centrifugal (Horizontal) ¦ Original material text: S1 – Carbon steel casing, cast iron trim (API 610) ¦ PZN2 review 1405-07: Supply overhead ×1.18 and VAT 10% are applied on top of unit prices (PUMPS G30:H31) | Y
109 | Fire Water Loading Pump | Pazanan 2 | P-191 | ROT-FIR | N/A (non-API 610) | I-2 | 33 | 31 |  | 4.6458 | ISO 5199 + IPS-M-PM-115 | ISO 5199 | IPS-M-PM-115 | N | Not stated | Not stated | Not stated | Electric Motor | Fire Water | 1 | Centrifugal | 2.9 | Not stated | 1404 | EUR | 16000 | 16000 | 16892.5293 | 11124288000 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | FOB | 16000 | 16892.5293 | 11124288000 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 0.8 | 1 | 1 | 1 | 0.8 | 20000 | 123.416 | 123.416 | N | 20000 | 7957.8364 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', cells A23:F23 (spec in B23, price in F23) | Type: Centrifugal (Horizontal) ¦ Driver: موتور الکتریکی (E) ¦ Head: 31 m ¦ کد پروژه 03229 ¦ FEED Report ¦ Original type text: Centrifugal (Horizontal) ¦ Original material text: I2 – Cast iron casing, bronze trim (API 610) ¦ PZN2 review 1405-07: Supply overhead ×1.18 and VAT 10% are applied on top of unit prices (PUMPS G30:H31) | Y
110 | Fire Water Pump-Elect. Motor Driven | Pazanan 2 | P-192 | ROT-FIR | BB (unspecified) | I-2 | 825 | 107 |  | 400.8856 | NFPA 20 + IPS-M-PM-125 | NFPA 20 | IPS-M-PM-125 | N | Not stated | Not stated | Not stated | Electric Motor | Fire Water | 1 | Centrifugal | 11.3 | Not stated | 1404 | EUR | 309660.11 | 309660.11 | 326933.9051 | 215296765359.48 | Vendor inquiry 1404Q1 – average of 3 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | FOB | 309660.11 | 326933.9051 | 215296765359.48 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 0.8 | 1 | 1 | 1 | 0.8 | 387075.1375 | 123.416 | 123.416 | N | 387075.1375 | 10616.5407 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', cells A24:F24 (spec in B24, price in F24) | Type: Centrifugal (Horizontal, ¦ Driver: موتور الکتریکی (E) ¦ Head: 107 m ¦ کد پروژه 03229 ¦ FEED Report ¦ Original type text: Centrifugal (Horizontal, Impeller Between Bearings Design) ¦ Original material text: I2 – Cast iron casing, bronze trim (API 610) ¦ PZN2 review 1405-07: Supply overhead ×1.18 and VAT 10% are applied on top of unit prices (PUMPS G30:H31) | Y
111 | Fire Water Pump-Diesel Engine Driven | Pazanan 2 | P-193 | ROT-FIR | BB (unspecified) | I-2 | 825 | 107 |  | 400.8856 | NFPA 20 + IPS-M-PM-125 | NFPA 20 | IPS-M-PM-125 | N | Not stated | Not stated | Not stated | Diesel Engine | Fire Water | 1 | Centrifugal | 11.3 | Not stated | 1404 | EUR | 202973.76 | 202973.76 | 214296.2618 | 141121160167.68 | Vendor inquiry 1404Q1 – average of 3 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | FOB | 202973.76 | 214296.2618 | 141121160167.68 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 0.8 | 1 | 1.35 | 1 | 1.08 | 187938.6667 | 123.416 | 123.416 | N | 187938.6667 | 5154.7059 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', cells A25:F25 (spec in B25, price in F25) | Type: Centrifugal (Horizontal, ¦ Driver: دیزلی (Diesel Engine) ¦ Head: 107 m ¦ کد پروژه 03229 ¦ FEED Report ¦ Original type text: Centrifugal (Horizontal, Impeller Between Bearings Design) ¦ Original material text: I2 – Cast iron casing, bronze trim (API 610) ¦ PZN2 review 1405-07: Supply overhead ×1.18 and VAT 10% are applied on top of unit prices (PUMPS G30:H31) | Y
112 | Fire Water Jockey Pumps | Pazanan 2 | P-194 A/B | ROT-FIR | OH (unspecified) | I-2 | 16.5 | 107 |  | 8.0177 | NFPA 20 + IPS-M-PM-125 | NFPA 20 | IPS-M-PM-125 | N | Not stated | Not stated | Not stated | Electric Motor | Fire Water | 2 | Centrifugal | 11.3 | Not stated | 1404 | EUR | 26808.07 | 26808.07 | 28303.5068 | 18638793212.76 | Vendor inquiry 1404Q1 – average of 3 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | FOB | 26808.07 | 28303.5068 | 18638793212.76 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 0.8 | 1 | 1 | 1 | 0.8 | 33510.0875 | 123.416 | 123.416 | N | 33510.0875 | 9610.4853 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', cells A26:F26 (spec in B26, price in F26) | Type: Centrifugal ¦ Driver: موتور الکتریکی (E) ¦ Head: 107 m ¦ کد پروژه 03229 ¦ FEED Report ¦ Original type text: Centrifugal (Horizontal, Overhung Impeller Design) ¦ Original material text: I2 – Cast iron casing, bronze trim (API 610) ¦ PZN2 review 1405-07: Supply overhead ×1.18 and VAT 10% are applied on top of unit prices (PUMPS G30:H31) | Y
113 | Chemical Loading Pumps | Pazanan 2 | P-210 A/B | ROT-AUX | N/A (non-API 610) | SS316L (non-API) | 9.6 |  |  |  | Not stated | Not stated | None | N | Not stated | Not stated | Not stated | Portable (Air / Electric) | Chemical | 2 | Portable Barrel |  | Not stated | 1393 | IRR | 100000000 | 2467.2595 | 3225.8065 | 100000000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AQ (IRR) – no 1404 quotation received (all vendors declined) | Not stated | 3333.4351 | 3519.3844 | 2317630742.0465 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; Size driver missing; | 1.35 | 1 | 1 | 1 | 1.35 | 1827.5996 | 91.347 | 123.416 | N | 2469.2112 |  | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', cells A27:F27 (spec in B27, price in F27) | Type: Portable Barrel Pump ¦ Driver: موتور پرتابل بادی/الکتریکی ¦ کد پروژه 03229 ¦ FEED Report ¦ Original type text: Portable Barrel Pump ¦ Original material text: S.S. 316 L – Stainless steel 316L (pump material, not an API class) ¦ PZN2 review 1405-07: Price reset to the 1393 base (100,000,000 IRR) because the 1404 figure was only an escalation of it – avoids double escalation; flow corrected 160 → 9.6 m3/h ¦ PZN2 review 1405-07: Supply overhead ×1.18 and VAT 10% are applied on top of unit prices (PUMPS G30:H31) | Y
114 | Chemical Loading Pumps | Pazanan 2 | P-211 | ROT-AUX | N/A (non-API 610) | SS316L (non-API) | 9.6 |  |  |  | Not stated | Not stated | None | N | Not stated | Not stated | Not stated | Portable (Air / Electric) | Chemical | 1 | Portable Barrel |  | Not stated | 1393 | IRR | 100000000 | 2467.2595 | 3225.8065 | 100000000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AQ (IRR) – no 1404 quotation received (all vendors declined) | Not stated | 3333.4351 | 3519.3844 | 2317630742.0465 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; Size driver missing; | 1.35 | 1 | 1 | 1 | 1.35 | 1827.5996 | 91.347 | 123.416 | N | 2469.2112 |  | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', cells A28:F28 (spec in B28, price in F28) | Type: Portable Barrel Pump ¦ Driver: موتور پرتابل بادی/الکتریکی ¦ کد پروژه 03229 ¦ FEED Report ¦ Original type text: Portable Barrel Pump ¦ Original material text: S.S. 316 L – Stainless steel 316L (pump material, not an API class) ¦ PZN2 review 1405-07: Price reset to the 1393 base (100,000,000 IRR) because the 1404 figure was only an escalation of it – avoids double escalation; flow corrected 160 → 9.6 m3/h ¦ PZN2 review 1405-07: Supply overhead ×1.18 and VAT 10% are applied on top of unit prices (PUMPS G30:H31) | Y
115 | 2nd Stage Separators Oil Pumps | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-CRU | Not stated | Not stated |  | 95.8 | 54.3 | 54.3 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Crude Oil | 1 | Centrifugal |  | Shaft (Absorbed) | (Not stated) | USD | 580000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | File نمونه قیمتی نمک زدایی overall.xlsx, sheet 'PUMPS', cells A4:H4 (price in H4) | Type: Centrifugal ¦ Driver: Electric motor (E) ¦ Power: 54.3 (Shaft) ¦ Head: 95.8 m ¦ Fluid: Crude Oil ¦ Quantity not stated in source; 1 assumed. ¦ Original type text: Centrifugal | Y
116 | 3rd Stage Separators Oil Pumps | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-CRU | Not stated | Not stated |  | 59.85 | 33.12 | 33.12 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Crude Oil | 1 | Centrifugal |  | Shaft (Absorbed) | (Not stated) | USD | 380000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | File نمونه قیمتی نمک زدایی overall.xlsx, sheet 'PUMPS', cells A5:H5 (price in H5) | Type: Centrifugal ¦ Driver: Electric motor (E) ¦ Power: 33.12 (Shaft) ¦ Head: 59.9 m ¦ Fluid: Crude Oil ¦ Quantity not stated in source; 1 assumed. ¦ Original type text: Centrifugal | Y
117 | Stabilized Oil Pump | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-CRU | Not stated | Not stated |  | 34.75 | 57.35 | 57.35 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Crude Oil | 1 | Centrifugal |  | Shaft (Absorbed) | (Not stated) | USD | 250000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | File نمونه قیمتی نمک زدایی overall.xlsx, sheet 'PUMPS', cells A6:H6 (price in H6) | Type: Centrifugal ¦ Driver: Electric motor (E) ¦ Power: 57.35 (Shaft) ¦ Head: 34.8 m ¦ Fluid: Stabilized Oil ¦ Quantity not stated in source; 1 assumed. ¦ Original type text: Centrifugal | Y
118 | Product Oil Pump | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-CRU | Not stated | Not stated |  |  |  |  | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Crude Oil | 1 | Centrifugal |  | Not stated | (Not stated) | USD | 320000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Size driver missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | File نمونه قیمتی نمک زدایی overall.xlsx, sheet 'PUMPS', cells A7:H7 (price in H7) | Type: Centrifugal ¦ Driver: Electric motor (E) ¦ Power: HOLD ¦ Fluid: Stabilized Oil ¦ Quantity not stated in source; 1 assumed. ¦ Power column in source = HOLD ¦ Original type text: Centrifugal | Y
119 | Off Spec Crude Pump | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-CRU | Not stated | Not stated |  | 311.3 | 48 | 48 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Crude Oil | 1 | Centrifugal |  | Shaft (Absorbed) | (Not stated) | USD | 75000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | File نمونه قیمتی نمک زدایی overall.xlsx, sheet 'PUMPS', cells A8:H8 (price in H8) | Type: Centrifugal ¦ Driver: Electric motor (E) ¦ Power: 48 (Shaft) ¦ Head: 311.3 m ¦ Fluid: off Crude ¦ Quantity not stated in source; 1 assumed. ¦ Original type text: Centrifugal | Y
120 | Second Stage Desalter Water Criculated Pump | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-WAT | Not stated | Not stated |  | 32 | 1 | 1 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Process / Dilution Water | 1 | Centrifugal |  | Shaft (Absorbed) | (Not stated) | USD | 60000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | File نمونه قیمتی نمک زدایی overall.xlsx, sheet 'PUMPS', cells A9:H9 (price in H9) | Type: Centrifugal ¦ Driver: Electric motor (E) ¦ Power: 1 (Shaft) ¦ Head: 32.0 m ¦ Fluid: Salty Water ¦ Quantity not stated in source; 1 assumed. ¦ Original type text: Centrifugal | Y
121 | Degassing Water Pump | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-WAT | Not stated | Not stated |  | 36.15 | 13.1 | 13.1 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Process / Dilution Water | 1 | Centrifugal |  | Shaft (Absorbed) | (Not stated) | USD | 60000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | File نمونه قیمتی نمک زدایی overall.xlsx, sheet 'PUMPS', cells A10:H10 (price in H10) | Type: Centrifugal ¦ Driver: Electric motor (E) ¦ Power: 13.1 (Shaft) ¦ Head: 36.2 m ¦ Fluid: Water ¦ Quantity not stated in source; 1 assumed. ¦ Original type text: Centrifugal | Y
122 | Disposal Water Pump | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-INJ | Not stated | Not stated |  | 51.5 |  |  | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Produced / Disposal Water | 1 | Centrifugal |  | Not stated | (Not stated) | USD | 10000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Size driver missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | File نمونه قیمتی نمک زدایی overall.xlsx, sheet 'PUMPS', cells A11:H11 (price in H11) | Type: Centrifugal ¦ Driver: Electric motor (E) ¦ Head: 51.5 m ¦ Fluid: Salty Water ¦ Quantity not stated in source; 1 assumed. ¦ Original type text: Centrifugal | Y
123 | Fresh Water Pump | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-WAT | Not stated | Not stated |  | 41 | 3.9 | 3.9 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Fresh / Potable Water | 1 | Centrifugal |  | Shaft (Absorbed) | (Not stated) | USD | 8000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | File نمونه قیمتی نمک زدایی overall.xlsx, sheet 'PUMPS', cells A12:H12 (price in H12) | Type: Centrifugal ¦ Driver: Electric motor (E) ¦ Power: 3.9 Shaft ¦ Head: 41.0 m ¦ Fluid: Water ¦ Quantity not stated in source; 1 assumed. ¦ Original type text: Centrifugal | Y
124 | Closed Drain Pump | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-DRN | Not stated | Not stated |  | 120 | 13.7 | 13.7 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Oily Water / Drain | 1 | Centrifugal |  | Not stated | (Not stated) | USD | 40000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | File نمونه قیمتی نمک زدایی overall.xlsx, sheet 'PUMPS', cells A13:H13 (price in H13) | Driver: Electric motor (E) ¦ Power: 13.7 ¦ Head: 120.0 m ¦ Fluid: HC ¦ Quantity not stated in source; 1 assumed. ¦ Original type text: Centrifugal (assumed) | Y
125 | Diesel Unlodaing pump | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-AUX | N/A (non-API 610) | Not stated |  | 27.2 |  |  | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Not stated | Diesel / Fuel Oil | 1 | PD-Rotary (Sliding Vane) |  | Not stated | (Not stated) | USD | 5000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Size driver missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | File نمونه قیمتی نمک زدایی overall.xlsx, sheet 'PUMPS', cells A14:H14 (price in H14) | Type: Sliding valve ¦ Driver: (Not stated) ¦ Head: 27.2 m ¦ Fluid: Diesel ¦ Quantity not stated in source; 1 assumed. ¦ Original type text: Sliding valve | Y
126 | Diesel Transfer pump | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-AUX | N/A (non-API 610) | Not stated |  | 40.8 | 0.83 | 0.83 | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Diesel / Fuel Oil | 1 | PD-Rotary (Screw) |  | Not stated | (Not stated) | USD | 3000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | File نمونه قیمتی نمک زدایی overall.xlsx, sheet 'PUMPS', cells A15:H15 (price in H15) | Type: Screw ¦ Driver: Electric motor (E) ¦ Power: 0.8 ¦ Head: 40.8 m ¦ Fluid: Diesel ¦ Quantity not stated in source; 1 assumed. ¦ Original type text: Screw | Y
127 | Sludge Discharge Water Jet Pump | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-WAT | Not stated | Not stated |  |  |  |  | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Process / Dilution Water | 1 | Centrifugal |  | Not stated | (Not stated) | USD | 3000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Size driver missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | File نمونه قیمتی نمک زدایی overall.xlsx, sheet 'PUMPS', cells A16:H16 (price in H16) | Type: Centrifugal ¦ Driver: Electric motor (E) ¦ Fluid: Water ¦ Quantity not stated in source; 1 assumed. ¦ Original type text: Centrifugal | Y
128 | Flare KO Drum Pumps | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-DRN | Not stated | Not stated |  |  |  |  | Not stated | Not stated | None | Not stated | Not stated | Not stated | Not stated | Electric Motor | Oily Water / Drain | 1 | Centrifugal |  | Not stated | (Not stated) | USD | 40000 | (Cost year not stated) | (Cost year not stated) | (Cost year not stated) | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | Not stated | (PPI/FX missing) |  |  | (Not stated in source document) | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Material missing; Seal missing; Size driver missing; Base-year PPI missing; | 1 | 1 | 1 | 1 | 1 |  |  | 123.416 | N |  |  | File نمونه قیمتی نمک زدایی overall.xlsx, sheet 'PUMPS', cells A17:H17 (price in H17) | Type: Centrifugal ¦ Driver: Electric motor (E) ¦ Quantity not stated in source; 1 assumed. ¦ Original type text: Centrifugal | Y
129 | Off Spec. Crude Pumps | Pazanan 2 | P-111 A/B | ROT-CRU | VS6 | D-1 | 45 | 139.1 |  | 28.4264 | API 610 + IPS-G-PM-105 + NACE MR0175 | API 610 | IPS-G-PM-105 | Y | Not stated | Not stated | Not stated | Electric Motor | Crude Oil | 2 | Centrifugal | 14.5 | Not stated | 1393 | EUR | 75000 | 75000 | 98058.3871 | 3039810000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | FOB | 101330.0929 | 106982.5978 | 70451571059.8049 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 1.7 | 1 | 1.05 | 1 | 1.785 | 42016.8067 | 91.347 | 123.416 | Y | 56767.5591 | 7618.4535 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', spec B8, R02 (1393) FOB price AR8 | Paired historical record of Row 94 (same tag & spec, 1404 inquiry price). Added 1405-07 for escalation / factor calibration. NOTE: counted in totals together with Row 94 – set Include=N if a single price per tag is needed. | Y
130 | Deaerated Water Pumps | Pazanan 2 | P-122 A/B | ROT-WAT | N/A (non-API 610) | I-2 | 53 | 35.7 |  | 8.5926 | ISO 5199 + IPS-M-PM-115 | ISO 5199 | IPS-M-PM-115 | N | Not stated | Not stated | Not stated | Electric Motor | Deaerated Water | 2 | Centrifugal | 2.9 | Not stated | 1393 | EUR | 10000 | 10000 | 13074.4516 | 405308000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | FOB | 13510.6791 | 14264.3464 | 9393542807.974 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 0.8 | 1 | 1 | 1 | 0.8 | 12500 | 91.347 | 123.416 | N | 16888.3488 | 4646.3415 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', spec B9, R02 (1393) FOB price AR9 | Paired historical record of Row 95 (same tag & spec, 1404 inquiry price). Added 1405-07 for escalation / factor calibration. NOTE: counted in totals together with Row 95 – set Include=N if a single price per tag is needed. | Y
131 | Dilution Water Pump | Pazanan 2 | P-124 | ROT-WAT | OH2 | I-2 | 53 | 122.3 |  | 29.4364 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Process / Dilution Water | 1 | Centrifugal | 12 | Not stated | 1393 | EUR | 15000 | 15000 | 19611.6774 | 607962000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | FOB | 20266.0186 | 21396.5196 | 14090314211.961 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 0.8 | 1 | 1 | 1 | 0.8 | 18750 | 91.347 | 123.416 | N | 25332.5232 | 3329.2579 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', spec B10, R02 (1393) FOB price AR10 | Paired historical record of Row 96 (same tag & spec, 1404 inquiry price). Added 1405-07 for escalation / factor calibration. NOTE: counted in totals together with Row 96 – set Include=N if a single price per tag is needed. | Y
132 | Dilution Water Pumps | Pazanan 2 | P-125 A/B | ROT-WAT | OH2 | I-2 | 31 | 122 |  | 17.1753 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Process / Dilution Water | 2 | Centrifugal | 13 | Not stated | 1393 | EUR | 12000 | 12000 | 15689.3419 | 486369600 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | FOB | 16212.8149 | 17117.2156 | 11272251369.5688 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 0.8 | 1 | 1 | 1 | 0.8 | 15000 | 91.347 | 123.416 | N | 20266.0186 | 3679.8144 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', spec B11, R02 (1393) FOB price AR11 | Paired historical record of Row 97 (same tag & spec, 1404 inquiry price). Added 1405-07 for escalation / factor calibration. NOTE: counted in totals together with Row 97 – set Include=N if a single price per tag is needed. | Y
133 | Disposal Water InjectionPumps | Pazanan 2 | P-136 A/B | ROT-INJ | BB3 | D-2 | 91 | 650 |  | 268.6194 | API 610 + IPS-G-PM-105 + NACE MR0175 | API 610 | IPS-G-PM-105 | Y | Not stated | Not stated | Not stated | Electric Motor | Produced / Disposal Water | 2 | Centrifugal | 72.8 | Not stated | 1393 | EUR | 260000 | 260000 | 339935.7419 | 10538008000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | FOB | 351277.6555 | 370873.0056 | 244232113007.3237 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 1.9 | 1 | 1.05 | 1 | 1.995 | 130325.8145 | 91.347 | 123.416 | Y | 176079.0253 | 6140.803 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', spec B12, R02 (1393) FOB price AR12 | Paired historical record of Row 98 (same tag & spec, 1404 inquiry price). Added 1405-07 for escalation / factor calibration. NOTE: counted in totals together with Row 98 – set Include=N if a single price per tag is needed. | Y
134 | Dirty Oil Pumps | Pazanan 2 | P-137 A/B | ROT-DRN | N/A (non-API 610) | D-1 | 5 |  |  |  | API 676 + IPS-M-PM-140 + NACE MR0175 | API 676 | IPS-M-PM-140 | Y | Not stated | Not stated | Not stated | Electric Motor | Slop / Dirty Oil | 2 | PD-Rotary (Gear) | 8 | Not stated | 1393 | EUR | 10000 | 10000 | 13074.4516 | 405308000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | FOB | 13510.6791 | 14264.3464 | 9393542807.974 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; Size driver missing; | 1.7 | 1 | 1.05 | 1 | 1.785 | 5602.2409 | 91.347 | 123.416 | N | 7569.0079 |  | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', spec B13, R02 (1393) FOB price AR13 | Paired historical record of Row 99 (same tag & spec, 1404 inquiry price). Added 1405-07 for escalation / factor calibration. NOTE: counted in totals together with Row 99 – set Include=N if a single price per tag is needed. | Y
135 | Evaporation Pond Water Return Pumps | Pazanan 2 | P-138 A/B | ROT-INJ | OH2 | D-2 | 15 | 27 |  | 1.8392 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Produced / Disposal Water | 2 | Centrifugal | 3.2 | Not stated | 1393 | EUR | 35000 | 35000 | 45760.5806 | 1418578000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | FOB | 47287.3767 | 49925.2123 | 32877399827.909 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 1.9 | 1 | 1 | 1 | 1.9 | 18421.0526 | 91.347 | 123.416 | Y | 24888.093 | 17266.6862 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', spec B14, R02 (1393) FOB price AR14 | Paired historical record of Row 100 (same tag & spec, 1404 inquiry price). Added 1405-07 for escalation / factor calibration. NOTE: counted in totals together with Row 100 – set Include=N if a single price per tag is needed. | Y
136 | Disposal Water InjectionPumps | Pazanan 2 | P-139 A/B/C | ROT-INJ | BB3 | D-2 | 44 | 385 |  | 76.9301 | API 610 + IPS-G-PM-105 + NACE MR0175 | API 610 | IPS-G-PM-105 | Y | Not stated | Not stated | Not stated | Electric Motor | Produced / Disposal Water | 3 | Centrifugal | 48.2 | Not stated | 1393 | EUR | 180000 | 180000 | 235340.129 | 7295544000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | FOB | 243192.2231 | 256758.2347 | 169083770543.5318 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 1.9 | 1 | 1.05 | 1 | 1.995 | 90225.5639 | 91.347 | 123.416 | Y | 121900.8637 | 9002.2098 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', spec B15, R02 (1393) FOB price AR15 | Paired historical record of Row 101 (same tag & spec, 1404 inquiry price). Added 1405-07 for escalation / factor calibration. NOTE: counted in totals together with Row 101 – set Include=N if a single price per tag is needed. | Y
137 | Flare K.O. Drum Pumps | Pazanan 2 | P-151 A/B | ROT-DRN | OH2 | S-6 | 10 | 40 |  | 1.8165 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Oily Water / Drain | 2 | Centrifugal | 6.8 | Not stated | 1393 | EUR | 15000 | 15000 | 19611.6774 | 607962000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | FOB | 25000 | 26394.577 | 17381700000 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 1.1 | 1 | 1 | 1 | 1.1 | 13636.3636 | 91.347 | 123.416 | Y | 22727.2727 | 15885.5303 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', spec B16, R02 (1393) FOB price AR16 | Paired historical record of Row 102 (same tag & spec, 1404 inquiry price). Added 1405-07 for escalation / factor calibration. NOTE: counted in totals together with Row 102 – set Include=N if a single price per tag is needed. | Y
138 | Closed Drain Drum Pumps | Pazanan 2 | P-161 A/B | ROT-DRN | OH2 | D-2 | 25 | 55 |  | 6.2443 | API 610 + IPS-G-PM-105 + NACE MR0175 | API 610 | IPS-G-PM-105 | Y | Not stated | Not stated | Not stated | Electric Motor | Oily Water / Drain | 2 | Centrifugal | 5 | Not stated | 1393 | EUR | 32000 | 32000 | 41838.2452 | 1296985600 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | FOB | 43234.173 | 45645.9084 | 30059336985.5168 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 1.9 | 1 | 1.05 | 1 | 1.995 | 16040.1003 | 91.347 | 123.416 | Y | 21671.2647 | 7220.9282 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', spec B17, R02 (1393) FOB price AR17 | Paired historical record of Row 103 (same tag & spec, 1404 inquiry price). Added 1405-07 for escalation / factor calibration. NOTE: counted in totals together with Row 103 – set Include=N if a single price per tag is needed. | Y
139 | C. D. Drum / Flare K.O. Drum Sump Pump | Pazanan 2 | P-162 | ROT-DRN | VS4 | S-6 | 5 | 21.4 |  | 0.48592 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Oily Water / Drain | 1 | Centrifugal | 2 | Not stated | 1393 | EUR | 15000 | 15000 | 19611.6774 | 607962000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | FOB | 25000 | 26394.577 | 17381700000 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 1.1 | 1 | 1 | 1 | 1.1 | 13636.3636 | 91.347 | 123.416 | Y | 22727.2727 | 35043.4976 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', spec B18, R02 (1393) FOB price AR18 | Paired historical record of Row 104 (same tag & spec, 1404 inquiry price). Added 1405-07 for escalation / factor calibration. NOTE: counted in totals together with Row 104 – set Include=N if a single price per tag is needed. | Y
140 | O.W.S. Water Pumps | Pazanan 2 | P-164 A/B | ROT-WAT | OH2 | D-2 | 15 | 50 |  | 3.406 | API 610 + IPS-G-PM-105 + NACE MR0175 | API 610 | IPS-G-PM-105 | Y | Not stated | Not stated | Not stated | Electric Motor | Oily Water / Drain | 2 | Centrifugal | 5.7 | Not stated | 1393 | EUR | 15000 | 15000 | 19611.6774 | 607962000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | FOB | 25000 | 26394.577 | 17381700000 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 1.9 | 1 | 1.05 | 1 | 1.995 | 7518.797 | 91.347 | 123.416 | Y | 12531.3283 | 6006.9047 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', spec B20, R02 (1393) FOB price AR20 | Paired historical record of Row 106 (same tag & spec, 1404 inquiry price). Added 1405-07 for escalation / factor calibration. NOTE: counted in totals together with Row 106 – set Include=N if a single price per tag is needed. | Y
141 | Oily Water Basin Pumps | Pazanan 2 | P-165 A/B | ROT-DRN | OH2 | S-6 | 15 | 20 |  | 1.3624 | API 610 + IPS-G-PM-105 | API 610 | IPS-G-PM-105 | N | Not stated | Not stated | Not stated | Electric Motor | Oily Water / Drain | 2 | Centrifugal | 2.5 | Not stated | 1393 | EUR | 15000 | 15000 | 19611.6774 | 607962000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | FOB | 25000 | 26394.577 | 17381700000 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 1.1 | 1 | 1 | 1 | 1.1 | 13636.3636 | 91.347 | 123.416 | Y | 22727.2727 | 18878.3902 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', spec B21, R02 (1393) FOB price AR21 | Paired historical record of Row 107 (same tag & spec, 1404 inquiry price). Added 1405-07 for escalation / factor calibration. NOTE: counted in totals together with Row 107 – set Include=N if a single price per tag is needed. | Y
142 | Fuel Oil Pump | Pazanan 2 | P-171 | ROT-AUX | N/A (non-API 610) | S-1 | 10 | 21 |  | 0.95368 | ISO 5199 + IPS-M-PM-115 | ISO 5199 | IPS-M-PM-115 | N | Not stated | Not stated | Not stated | Electric Motor | Diesel / Fuel Oil | 1 | Centrifugal | 2 | Not stated | 1393 | EUR | 10000 | 10000 | 13074.4516 | 405308000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | FOB | 13510.6791 | 14264.3464 | 9393542807.974 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 0.9 | 1 | 1 | 1 | 0.9 | 11111.1111 | 91.347 | 123.416 | N | 15011.8656 | 15445.198 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', spec B22, R02 (1393) FOB price AR22 | Paired historical record of Row 108 (same tag & spec, 1404 inquiry price). Added 1405-07 for escalation / factor calibration. NOTE: counted in totals together with Row 108 – set Include=N if a single price per tag is needed. | Y
143 | Fire Water Loading Pump | Pazanan 2 | P-191 | ROT-FIR | N/A (non-API 610) | I-2 | 33 | 31 |  | 4.6458 | ISO 5199 + IPS-M-PM-115 | ISO 5199 | IPS-M-PM-115 | N | Not stated | Not stated | Not stated | Electric Motor | Fire Water | 1 | Centrifugal | 2.9 | Not stated | 1393 | EUR | 6500 | 6500 | 8498.3935 | 263450200 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | FOB | 8781.9414 | 9271.8251 | 6105802825.1831 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 0.8 | 1 | 1 | 1 | 0.8 | 8125 | 91.347 | 123.416 | N | 10977.4267 | 4367.8283 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', spec B23, R02 (1393) FOB price AR23 | Paired historical record of Row 109 (same tag & spec, 1404 inquiry price). Added 1405-07 for escalation / factor calibration. NOTE: counted in totals together with Row 109 – set Include=N if a single price per tag is needed. | Y
144 | Fire Water Pump-Elect. Motor Driven | Pazanan 2 | P-192 | ROT-FIR | BB (unspecified) | I-2 | 825 | 107 |  | 400.8856 | NFPA 20 + IPS-M-PM-125 | NFPA 20 | IPS-M-PM-125 | N | Not stated | Not stated | Not stated | Electric Motor | Fire Water | 1 | Centrifugal | 11.3 | Not stated | 1393 | EUR | 80000 | 80000 | 104595.6129 | 3242464000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | FOB | 108085.4325 | 114114.771 | 75148342463.7919 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 0.8 | 1 | 1 | 1 | 0.8 | 100000 | 91.347 | 123.416 | N | 135106.7906 | 3705.6545 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', spec B24, R02 (1393) FOB price AR24 | Paired historical record of Row 110 (same tag & spec, 1404 inquiry price). Added 1405-07 for escalation / factor calibration. NOTE: counted in totals together with Row 110 – set Include=N if a single price per tag is needed. | Y
145 | Fire Water Pump-Diesel Engine Driven | Pazanan 2 | P-193 | ROT-FIR | BB (unspecified) | I-2 | 825 | 107 |  | 400.8856 | NFPA 20 + IPS-M-PM-125 | NFPA 20 | IPS-M-PM-125 | N | Not stated | Not stated | Not stated | Diesel Engine | Fire Water | 1 | Centrifugal | 11.3 | Not stated | 1393 | EUR | 100000 | 100000 | 130744.5161 | 4053080000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | FOB | 135106.7906 | 142643.4637 | 93935428079.7399 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 0.8 | 1 | 1.35 | 1 | 1.08 | 92592.5926 | 91.347 | 123.416 | N | 125098.8802 | 3431.1616 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', spec B25, R02 (1393) FOB price AR25 | Paired historical record of Row 111 (same tag & spec, 1404 inquiry price). Added 1405-07 for escalation / factor calibration. NOTE: counted in totals together with Row 111 – set Include=N if a single price per tag is needed. | Y
146 | Fire Water Jockey Pumps | Pazanan 2 | P-194 A/B | ROT-FIR | OH (unspecified) | I-2 | 16.5 | 107 |  | 8.0177 | NFPA 20 + IPS-M-PM-125 | NFPA 20 | IPS-M-PM-125 | N | Not stated | Not stated | Not stated | Electric Motor | Fire Water | 2 | Centrifugal | 11.3 | Not stated | 1393 | EUR | 15000 | 15000 | 19611.6774 | 607962000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | FOB | 20266.0186 | 21396.5196 | 14090314211.961 | (Pazanan II Inquiry / Thermo Engineering) | Basic Design | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Not stated | Seal missing; | 0.8 | 1 | 1 | 1 | 0.8 | 18750 | 91.347 | 123.416 | N | 25332.5232 | 7265.2106 | File PC-ME 14040105 Pazanan2 Reconstruction.xlsx, sheet 'PUMPS', spec B26, R02 (1393) FOB price AR26 | Paired historical record of Row 112 (same tag & spec, 1404 inquiry price). Added 1405-07 for escalation / factor calibration. NOTE: counted in totals together with Row 112 – set Include=N if a single price per tag is needed. | Y
Note on A4: شناسه یکتای رکورد. Vendor_Quotes با همین شماره به رکورد وصل است.
Note on B4: نام سرویس پمپ طبق منبع (متن تکراری داخل پرانتز حذف شده و نام کامل زیرگروه در داشبورد آمده است).
Note on C4: پروژه مرجع.
Note on D4: شماره تگ طبق منبع.
Note on E4: زیرگروه پمپ. نام کامل و شرح در Executive Dashboard.
Note on F4: نوع پیکربندی طبق API 610 (OH / BB / VS). شرح هر نوع در Executive Dashboard. N/A یعنی پمپ API 610 نیست.
Note on G4: کلاس متریال طبق جدول H.1 استاندارد API 610. شرح هر کلاس در Note همان سلول و در Executive Dashboard.
Note on H4: دبی نامی (Rated Flow).
Note on I4: هد دیفرانسیل. سلول زرد = محاسبه‌شده از اختلاف فشار با فرض SG=1.
Note on J4: توان طبق منبع (موتور یا محور؛ نوع آن در ستون Power Basis).
Note on K4: اندازه مبنای مقایسه: اگر توان منبع موجود باشد همان، وگرنه Q×H/(367×η) با η=0.6 و SG=1.
Note on L4: همه استانداردهای رکورد در یک سلول (خودکار از ستون‌های جمع‌شده کنار آن: استاندارد اصلی، IPS و NACE).
Note on M4: استاندارد اصلی ساخت پمپ (ورودی).
Note on N4: استاندارد مکمل IPS وزارت نفت (ورودی).
Note on O4: الزام NACE MR0175 / ISO 15156 برای سرویس ترش (ورودی). زرد = استنباطی.
Note on P4: نوع آب‌بند مکانیکی طبق API 682: Arr 1 تکی، Arr 2 دوبل بدون فشار، Arr 3 دوبل تحت فشار.
Note on Q4: کلاس سختگیری آب‌بند طبق API 682: Cat 1 سبک، Cat 2 استاندارد API 610، Cat 3 سنگین.
Note on R4: طرح شستشو / Barrier آب‌بند طبق API 682 (مثلاً 11، 52، 53B).
Note on S4: نوع محرک.
Note on T4: سیالی که پمپ جابه‌جا می‌کند.
Note on U4: تعداد طبق منبع (Set).
Note on V4: اصل کارکرد پمپ (گریز از مرکز یا جابه‌جایی مثبت). پیکربندی در API 610 Type آمده است. زرد = فرض‌شده.
Note on W4: فشار رانش طبق منبع (در گچساران نوع فشار مشخص نیست).
Note on X4: نوع عدد توان: توان نامی موتور یا توان محور.
Note on Y4: سال مبنای قیمت مرجع.
Note on Z4: ارز قیمت مرجع.
Note on AA4: قیمت واحد در ارز و سال مرجع، عیناً از منبع.
Note on AB4: معادل یورویی قیمت مرجع در سال منبع، با نرخ جدول FX بانک.
Note on AC4: معادل دلاری قیمت مرجع در سال منبع، با نرخ جدول FX بانک.
Note on AD4: معادل ریالی قیمت مرجع در سال منبع، با نرخ جدول FX بانک. سلول آبی = پروژه نرخ دیگری به کار برده (نرخ و قیمت پروژه در Note).
Note on AE4: مبنای قیمت به نقل از منبع (استعلام، برآورد MTO، قیمت خرید و ...). برچسب کلاس منبع هم داخل همین متن آمده است.
Note on AF4: شرط تحویل قیمت. Note هر سلول می‌گوید قیمت شامل چه هزینه‌هایی هست و نیست. زرد = استنباطی. جدول حالت‌ها در Executive Dashboard.
Note on AG4: قیمت یورویی تعدیل‌شده به سال هدف: EUR × PPI(هدف)/PPI(پایه)، با کف ۲۵٬۰۰۰ یورو برای API 610 گریز از مرکز کلاس S/D.
Note on AH4: = قیمت یورویی تعدیل‌شده × نرخ یورو ÷ نرخ دلار سال هدف.
Note on AI4: = قیمت یورویی تعدیل‌شده × نرخ یوروی سال هدف.
Note on AJ4: سازنده یا تهیه‌کننده سند منبع.
Note on AK4: مرحله پروژه‌ای که سند منبع در آن تهیه شده.
Note on AL4: Scope: driver included (base = Y). Y/N/Not stated. زرد = استنباطی.
Note on AM4: Scope: baseplate & coupling (base = Y). Y/N/Not stated. زرد = استنباطی.
Note on AN4: Scope: seal support system (base = Y). Y/N/Not stated. زرد = استنباطی.
Note on AO4: Scope: commissioning spares (base = Y). Y/N/Not stated. زرد = استنباطی.
Note on AP4: Scope: 2-year spares (base = N). Y/N/Not stated. زرد = استنباطی.
Note on AQ4: Scope: third-party inspection (base = N). Y/N/Not stated. زرد = استنباطی.
Note on AR4: Scope: witnessed FAT (base = N). Y/N/Not stated. زرد = استنباطی.
Note on AS4: کنترل خودکار کمبود یا تناقض داده.
Note on AT4: ضریب متریال از Factors_ROT.
Note on AU4: Arrangement × Category × Plan.
Note on AV4: Driver × NACE.
Note on AW4: حاصل‌ضرب ۷ ضریب Scope.
Note on AX4: MAT × SEAL × DRIVE × SCOPE.
Note on AY4: EUR سال منبع ÷ ALL_F = قیمت معادل پیکربندی پایه.
Note on BB4: Y اگر استاندارد API 610، پمپ گریز از مرکز و کلاس متریال S-x یا D-x باشد.
Note on BD4: مبنای Estimator.
Note on BE4: فایل، شیت و سلول منبع.
Note on BG4: N = رکورد تکراری یا کنارگذاشته‌شده (در شمارش داشبورد و جستجو با فیلتر لحاظ نمی‌شود).
Note on E5: ROT-CRU = Crude Oil & Main Transfer Pumps پمپ‌های نفت خام: انتقال نفت شور و نمک‌زدایی‌شده، Booster، Off-spec و انتقال اصلی
Note on F5: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G5: کلاس متریال در منبع ذکر نشده است.
Note on I5: SOURCE – 18061405_Pump_only_CSV.csv line 5, column "Head (m)"
Note on S5: SOURCE – 18061405_Pump_only_CSV.csv line 5, column "Driver Type" = E
Note on AF5: شرط تحویل: در منبع ذکر نشده. این قیمت = «Price ($)» فایل CSV (قیمت خرید). هزینه گمرک و حمل جداگانه آمده و در این قیمت نیست: 14,400 دلار (CSV سطر 5، ستون J).
Note on E6: ROT-CRU = Crude Oil & Main Transfer Pumps پمپ‌های نفت خام: انتقال نفت شور و نمک‌زدایی‌شده، Booster، Off-spec و انتقال اصلی
Note on F6: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G6: کلاس متریال در منبع ذکر نشده است.
Note on I6: SOURCE – 18061405_Pump_only_CSV.csv line 6, column "Head (m)"
Note on S6: SOURCE – 18061405_Pump_only_CSV.csv line 6, column "Driver Type" = E
Note on AF6: شرط تحویل: در منبع ذکر نشده. این قیمت = «Price ($)» فایل CSV (قیمت خرید). هزینه گمرک و حمل جداگانه آمده و در این قیمت نیست: 16,800 دلار (CSV سطر 6، ستون J).
Note on E7: ROT-CRU = Crude Oil & Main Transfer Pumps پمپ‌های نفت خام: انتقال نفت شور و نمک‌زدایی‌شده، Booster، Off-spec و انتقال اصلی
Note on F7: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G7: کلاس متریال در منبع ذکر نشده است.
Note on I7: SOURCE – 18061405_Pump_only_CSV.csv line 7, column "Head (m)"
Note on S7: SOURCE – 18061405_Pump_only_CSV.csv line 7, column "Driver Type" = E
Note on AF7: شرط تحویل: در منبع ذکر نشده. این قیمت = «Price ($)» فایل CSV (قیمت خرید). هزینه گمرک و حمل جداگانه آمده و در این قیمت نیست: 15,000 دلار (CSV سطر 7، ستون J).
Note on E8: ROT-CRU = Crude Oil & Main Transfer Pumps پمپ‌های نفت خام: انتقال نفت شور و نمک‌زدایی‌شده، Booster، Off-spec و انتقال اصلی
Note on F8: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G8: کلاس متریال در منبع ذکر نشده است.
Note on I8: SOURCE – 18061405_Pump_only_CSV.csv line 8, column "Head (m)"
Note on S8: SOURCE – 18061405_Pump_only_CSV.csv line 8, column "Driver Type" = E
Note on AF8: شرط تحویل: در منبع ذکر نشده. این قیمت = «Price ($)» فایل CSV (قیمت خرید). هزینه گمرک و حمل جداگانه آمده و در این قیمت نیست: 25,200 دلار (CSV سطر 8، ستون J).
Note on E9: ROT-CRU = Crude Oil & Main Transfer Pumps پمپ‌های نفت خام: انتقال نفت شور و نمک‌زدایی‌شده، Booster، Off-spec و انتقال اصلی
Note on F9: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G9: کلاس متریال در منبع ذکر نشده است.
Note on I9: SOURCE – 18061405_Pump_only_CSV.csv line 9, column "Head (m)"
Note on S9: SOURCE – 18061405_Pump_only_CSV.csv line 9, column "Driver Type" = E
Note on AF9: شرط تحویل: در منبع ذکر نشده. این قیمت = «Price ($)» فایل CSV (قیمت خرید). هزینه گمرک و حمل جداگانه آمده و در این قیمت نیست: 4,500 دلار (CSV سطر 9، ستون J).
Note on E10: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F10: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G10: کلاس متریال در منبع ذکر نشده است.
Note on I10: SOURCE – 18061405_Pump_only_CSV.csv line 10, column "Head (m)"
Note on S10: SOURCE – 18061405_Pump_only_CSV.csv line 10, column "Driver Type" = E
Note on AF10: شرط تحویل: در منبع ذکر نشده. این قیمت = «Price ($)» فایل CSV (قیمت خرید). هزینه گمرک و حمل جداگانه آمده و در این قیمت نیست: 3,600 دلار (CSV سطر 10، ستون J).
Note on E11: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F11: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G11: کلاس متریال در منبع ذکر نشده است.
Note on I11: SOURCE – 18061405_Pump_only_CSV.csv line 11, column "Head (m)"
Note on S11: SOURCE – 18061405_Pump_only_CSV.csv line 11, column "Driver Type" = E
Note on AF11: شرط تحویل: در منبع ذکر نشده. این قیمت = «Price ($)» فایل CSV (قیمت خرید). هزینه گمرک و حمل جداگانه آمده و در این قیمت نیست: 3,600 دلار (CSV سطر 11، ستون J).
Note on E12: ROT-INJ = Produced Water & Disposal Injection Pumps آب تولیدی و پساب: Booster و پمپ‌های پرفشار تزریق به چاه دفعی
Note on F12: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G12: کلاس متریال در منبع ذکر نشده است.
Note on I12: SOURCE – 18061405_Pump_only_CSV.csv line 12, column "Head (m)"
Note on S12: SOURCE – 18061405_Pump_only_CSV.csv line 12, column "Driver Type" = E
Note on AF12: شرط تحویل: در منبع ذکر نشده. این قیمت = «Price ($)» فایل CSV (قیمت خرید). هزینه گمرک و حمل جداگانه آمده و در این قیمت نیست: 24,600 دلار (CSV سطر 12، ستون J).
Note on E13: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن — Reclassified 1405-07: ROT-DRN → ROT-WAT (service-based classification; approved)
Note on F13: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G13: کلاس متریال در منبع ذکر نشده است.
Note on I13: SOURCE – 18061405_Pump_only_CSV.csv line 13, column "Head (m)"
Note on S13: SOURCE – 18061405_Pump_only_CSV.csv line 13, column "Driver Type" = E
Note on AF13: شرط تحویل: در منبع ذکر نشده. این قیمت = «Price ($)» فایل CSV (قیمت خرید). هزینه گمرک و حمل جداگانه آمده و در این قیمت نیست: 480 دلار (CSV سطر 13، ستون J).
Note on E14: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن
Note on F14: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G14: کلاس متریال در منبع ذکر نشده است.
Note on I14: SOURCE – 18061405_Pump_only_CSV.csv line 14, column "Head (m)"
Note on S14: SOURCE – 18061405_Pump_only_CSV.csv line 14, column "Driver Type" = E
Note on AF14: شرط تحویل: در منبع ذکر نشده. این قیمت = «Price ($)» فایل CSV (قیمت خرید). هزینه گمرک و حمل جداگانه آمده و در این قیمت نیست: 2,400 دلار (CSV سطر 14، ستون J).
Note on E15: ROT-AUX = Chemical, Fuel & Auxiliary Pumps پمپ‌های جانبی: مواد شیمیایی، گلایکول، گازوئیل و سوخت
Note on F15: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G15: کلاس متریال در منبع ذکر نشده است.
Note on I15: SOURCE – 18061405_Pump_only_CSV.csv line 15, column "Head (m)"
Note on S15: SOURCE – 18061405_Pump_only_CSV.csv line 15, column "Driver Type" = E
Note on AF15: شرط تحویل: در منبع ذکر نشده. این قیمت = «Price ($)» فایل CSV (قیمت خرید). هزینه گمرک و حمل جداگانه آمده و در این قیمت نیست: 300 دلار (CSV سطر 15، ستون J).
Note on E16: ROT-AUX = Chemical, Fuel & Auxiliary Pumps پمپ‌های جانبی: مواد شیمیایی، گلایکول، گازوئیل و سوخت
Note on F16: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G16: کلاس متریال در منبع ذکر نشده است.
Note on I16: SOURCE – 18061405_Pump_only_CSV.csv line 16, column "Head (m)"
Note on S16: SOURCE – 18061405_Pump_only_CSV.csv line 16, column "Driver Type" = E
Note on AF16: شرط تحویل: در منبع ذکر نشده. این قیمت = «Price ($)» فایل CSV (قیمت خرید). هزینه گمرک و حمل جداگانه آمده و در این قیمت نیست: 180 دلار (CSV سطر 16، ستون J).
Note on E17: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F17: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G17: کلاس متریال در منبع ذکر نشده است.
Note on I17: SOURCE – 18061405_Pump_only_CSV.csv line 17, column "Head (m)"
Note on S17: SOURCE – 18061405_Pump_only_CSV.csv line 17, column "Driver Type" = E
Note on AF17: شرط تحویل: در منبع ذکر نشده. این قیمت = «Price ($)» فایل CSV (قیمت خرید). هزینه گمرک و حمل جداگانه آمده و در این قیمت نیست: 180 دلار (CSV سطر 17، ستون J).
Note on E18: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن
Note on F18: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G18: کلاس متریال در منبع ذکر نشده است.
Note on I18: SOURCE – 18061405_Pump_only_CSV.csv line 18, column "Head (m)"
Note on S18: SOURCE – 18061405_Pump_only_CSV.csv line 18, column "Driver Type" = E
Note on AF18: شرط تحویل: در منبع ذکر نشده. این قیمت = «Price ($)» فایل CSV (قیمت خرید). هزینه گمرک و حمل جداگانه آمده و در این قیمت نیست: 2,400 دلار (CSV سطر 18، ستون J).
Note on E19: ROT-CRU = Crude Oil & Main Transfer Pumps پمپ‌های نفت خام: انتقال نفت شور و نمک‌زدایی‌شده، Booster، Off-spec و انتقال اصلی
Note on F19: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G19: کلاس متریال در منبع ذکر نشده است.
Note on M19: PEP-Rev.140205 P.ME gives only flow / pressure / kW – no design standard stated (previous bank had "API 610 / IPS", unsupported)
Note on S19: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است (P.ME فقط توان kW را داده است)
Note on V19: INFERRED – source does not state pump type; "Centrifugal (assumed)" carried from previous bank
Note on W19: PEP P.ME: pressure given as "bar" – discharge / differential / design not specified
Note on Y19: INFERRED – PEP-Rev.140205 Gachsaran 4 PEP Rev.1402/05: IRR value is built with USD_Change_IRR = 420,000 ('basic data' B2 = 'Procurement' G1 'ارز مرجع'), i.e. the 1402 rate; base year of the EUR figure itself is not stated → 1402 assumed (previous bank had 1399 – not supported by the file)
Note on Z19: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H11: formula =ROUND(385000*per_Euro*USD_Change_IRR,-3) → base price is EUR (IRR value is only a conversion at per_Euro 1.085 × 420,000)
Note on AA19: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H11: EUR constant inside the formula
Note on AD19: نرخ پروژه: در فایل PEP-Rev.140205 گچساران ۴ (P.ME H11) قیمت با نرخ یورو 455,692 ریال (= ۴۲۰٬۰۰۰ ریال/دلار × ۱٫۰۸۵) برابر 175,441,330,000 ریال بوده است. این سلول با نرخ جدول FX بانک (سال ۱۴۰۲) محاسبه شده است.
Note on AF19: شرط تحویل: EXW (استنباطی). این قیمت = «هزینه واحد بدون ضریب» شیت P.ME سند PEP گچساران (Rev.1402/05). این قیمت شامل نیست (هر کدام سطر جداگانه دارند): حمل هر قلم (P.ME ستون N)، یدکی راه‌اندازی و دو ساله (Procurement D49)، بیمه ۱٪ (D51)، بارگیری و حمل ۳٪ (D52)، بازرسی شخص ثالث ۱٪ (D53)، خدمات فنی سازنده در نصب ۳٪ (D54)، بالاسری پروژه (EPC Summary، ستون «با اعمال سربار»)، نصب و مالیات.
Note on AO19: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AP19: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AQ19: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on E20: ROT-CRU = Crude Oil & Main Transfer Pumps پمپ‌های نفت خام: انتقال نفت شور و نمک‌زدایی‌شده، Booster، Off-spec و انتقال اصلی
Note on F20: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G20: کلاس متریال در منبع ذکر نشده است.
Note on M20: PEP-Rev.140205 P.ME gives only flow / pressure / kW – no design standard stated (previous bank had "API 610 / IPS", unsupported)
Note on S20: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است (P.ME فقط توان kW را داده است)
Note on V20: INFERRED – source does not state pump type; "Centrifugal (assumed)" carried from previous bank
Note on W20: PEP P.ME: pressure given as "bar" – discharge / differential / design not specified
Note on Y20: INFERRED – PEP-Rev.140205 Gachsaran 4 PEP Rev.1402/05: IRR value is built with USD_Change_IRR = 420,000 ('basic data' B2 = 'Procurement' G1 'ارز مرجع'), i.e. the 1402 rate; base year of the EUR figure itself is not stated → 1402 assumed (previous bank had 1399 – not supported by the file)
Note on Z20: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H12: formula =ROUND(135000*per_Euro*USD_Change_IRR,-3) → base price is EUR (IRR value is only a conversion at per_Euro 1.085 × 420,000)
Note on AA20: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H12: EUR constant inside the formula
Note on AD20: نرخ پروژه: در فایل PEP-Rev.140205 گچساران ۴ (P.ME H12) قیمت با نرخ یورو 455,692 ریال (= ۴۲۰٬۰۰۰ ریال/دلار × ۱٫۰۸۵) برابر 61,518,388,000 ریال بوده است. این سلول با نرخ جدول FX بانک (سال ۱۴۰۲) محاسبه شده است.
Note on AF20: شرط تحویل: EXW (استنباطی). این قیمت = «هزینه واحد بدون ضریب» شیت P.ME سند PEP گچساران (Rev.1402/05). این قیمت شامل نیست (هر کدام سطر جداگانه دارند): حمل هر قلم (P.ME ستون N)، یدکی راه‌اندازی و دو ساله (Procurement D49)، بیمه ۱٪ (D51)، بارگیری و حمل ۳٪ (D52)، بازرسی شخص ثالث ۱٪ (D53)، خدمات فنی سازنده در نصب ۳٪ (D54)، بالاسری پروژه (EPC Summary، ستون «با اعمال سربار»)، نصب و مالیات.
Note on AO20: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AP20: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AQ20: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on E21: ROT-CRU = Crude Oil & Main Transfer Pumps پمپ‌های نفت خام: انتقال نفت شور و نمک‌زدایی‌شده، Booster، Off-spec و انتقال اصلی
Note on F21: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G21: کلاس متریال در منبع ذکر نشده است.
Note on M21: PEP-Rev.140205 P.ME gives only flow / pressure / kW – no design standard stated (previous bank had "API 610 / IPS", unsupported)
Note on S21: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است (P.ME فقط توان kW را داده است)
Note on V21: INFERRED – source does not state pump type; "Centrifugal (assumed)" carried from previous bank
Note on W21: PEP P.ME: pressure given as "bar" – discharge / differential / design not specified
Note on Y21: INFERRED – PEP-Rev.140205 Gachsaran 4 PEP Rev.1402/05: IRR value is built with USD_Change_IRR = 420,000 ('basic data' B2 = 'Procurement' G1 'ارز مرجع'), i.e. the 1402 rate; base year of the EUR figure itself is not stated → 1402 assumed (previous bank had 1399 – not supported by the file)
Note on Z21: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H13: formula =ROUND(140000*per_Euro*USD_Change_IRR,-3) → base price is EUR (IRR value is only a conversion at per_Euro 1.085 × 420,000)
Note on AA21: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H13: EUR constant inside the formula
Note on AD21: نرخ پروژه: در فایل PEP-Rev.140205 گچساران ۴ (P.ME H13) قیمت با نرخ یورو 455,692 ریال (= ۴۲۰٬۰۰۰ ریال/دلار × ۱٫۰۸۵) برابر 63,796,847,232 ریال بوده است. این سلول با نرخ جدول FX بانک (سال ۱۴۰۲) محاسبه شده است.
Note on AF21: شرط تحویل: EXW (استنباطی). این قیمت = «هزینه واحد بدون ضریب» شیت P.ME سند PEP گچساران (Rev.1402/05). این قیمت شامل نیست (هر کدام سطر جداگانه دارند): حمل هر قلم (P.ME ستون N)، یدکی راه‌اندازی و دو ساله (Procurement D49)، بیمه ۱٪ (D51)، بارگیری و حمل ۳٪ (D52)، بازرسی شخص ثالث ۱٪ (D53)، خدمات فنی سازنده در نصب ۳٪ (D54)، بالاسری پروژه (EPC Summary، ستون «با اعمال سربار»)، نصب و مالیات.
Note on AO21: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AP21: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AQ21: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on E22: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F22: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G22: کلاس متریال در منبع ذکر نشده است.
Note on M22: PEP-Rev.140205 P.ME gives only flow / pressure / kW – no design standard stated (previous bank had "API 610 / IPS", unsupported)
Note on S22: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است (P.ME فقط توان kW را داده است)
Note on V22: INFERRED – source does not state pump type; "Centrifugal (assumed)" carried from previous bank
Note on W22: PEP P.ME: pressure given as "bar" – discharge / differential / design not specified
Note on Y22: INFERRED – PEP-Rev.140205 Gachsaran 4 PEP Rev.1402/05: IRR value is built with USD_Change_IRR = 420,000 ('basic data' B2 = 'Procurement' G1 'ارز مرجع'), i.e. the 1402 rate; base year of the EUR figure itself is not stated → 1402 assumed (previous bank had 1399 – not supported by the file)
Note on Z22: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H14: formula =ROUND(34000*per_Euro*USD_Change_IRR,-3) → base price is EUR (IRR value is only a conversion at per_Euro 1.085 × 420,000)
Note on AA22: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H14: EUR constant inside the formula
Note on AD22: نرخ پروژه: در فایل PEP-Rev.140205 گچساران ۴ (P.ME H14) قیمت با نرخ یورو 455,692 ریال (= ۴۲۰٬۰۰۰ ریال/دلار × ۱٫۰۸۵) برابر 15,493,520,000 ریال بوده است. این سلول با نرخ جدول FX بانک (سال ۱۴۰۲) محاسبه شده است.
Note on AF22: شرط تحویل: EXW (استنباطی). این قیمت = «هزینه واحد بدون ضریب» شیت P.ME سند PEP گچساران (Rev.1402/05). این قیمت شامل نیست (هر کدام سطر جداگانه دارند): حمل هر قلم (P.ME ستون N)، یدکی راه‌اندازی و دو ساله (Procurement D49)، بیمه ۱٪ (D51)، بارگیری و حمل ۳٪ (D52)، بازرسی شخص ثالث ۱٪ (D53)، خدمات فنی سازنده در نصب ۳٪ (D54)، بالاسری پروژه (EPC Summary، ستون «با اعمال سربار»)، نصب و مالیات.
Note on AO22: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AP22: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AQ22: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on E23: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F23: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G23: کلاس متریال در منبع ذکر نشده است.
Note on M23: PEP-Rev.140205 P.ME gives only flow / pressure / kW – no design standard stated (previous bank had "API 610 / IPS", unsupported)
Note on S23: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است (P.ME فقط توان kW را داده است)
Note on V23: INFERRED – source does not state pump type; "Centrifugal (assumed)" carried from previous bank
Note on W23: PEP P.ME: pressure given as "bar" – discharge / differential / design not specified
Note on Y23: INFERRED – PEP-Rev.140205 Gachsaran 4 PEP Rev.1402/05: IRR value is built with USD_Change_IRR = 420,000 ('basic data' B2 = 'Procurement' G1 'ارز مرجع'), i.e. the 1402 rate; base year of the EUR figure itself is not stated → 1402 assumed (previous bank had 1399 – not supported by the file)
Note on Z23: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H17: formula =ROUND(29000*per_Euro*USD_Change_IRR,-3) → base price is EUR (IRR value is only a conversion at per_Euro 1.085 × 420,000)
Note on AA23: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H17: EUR constant inside the formula
Note on AD23: نرخ پروژه: در فایل PEP-Rev.140205 گچساران ۴ (P.ME H17) قیمت با نرخ یورو 455,692 ریال (= ۴۲۰٬۰۰۰ ریال/دلار × ۱٫۰۸۵) برابر 13,215,061,212 ریال بوده است. این سلول با نرخ جدول FX بانک (سال ۱۴۰۲) محاسبه شده است.
Note on AF23: شرط تحویل: EXW (استنباطی). این قیمت = «هزینه واحد بدون ضریب» شیت P.ME سند PEP گچساران (Rev.1402/05). این قیمت شامل نیست (هر کدام سطر جداگانه دارند): حمل هر قلم (P.ME ستون N)، یدکی راه‌اندازی و دو ساله (Procurement D49)، بیمه ۱٪ (D51)، بارگیری و حمل ۳٪ (D52)، بازرسی شخص ثالث ۱٪ (D53)، خدمات فنی سازنده در نصب ۳٪ (D54)، بالاسری پروژه (EPC Summary، ستون «با اعمال سربار»)، نصب و مالیات.
Note on AO23: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AP23: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AQ23: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on E24: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F24: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G24: کلاس متریال در منبع ذکر نشده است.
Note on M24: PEP-Rev.140205 P.ME gives only flow / pressure / kW – no design standard stated (previous bank had "API 610 / IPS", unsupported)
Note on S24: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است (P.ME فقط توان kW را داده است)
Note on V24: INFERRED – source does not state pump type; "Centrifugal (assumed)" carried from previous bank
Note on W24: PEP P.ME: pressure given as "bar" – discharge / differential / design not specified
Note on Y24: INFERRED – PEP-Rev.140205 Gachsaran 4 PEP Rev.1402/05: IRR value is built with USD_Change_IRR = 420,000 ('basic data' B2 = 'Procurement' G1 'ارز مرجع'), i.e. the 1402 rate; base year of the EUR figure itself is not stated → 1402 assumed (previous bank had 1399 – not supported by the file)
Note on Z24: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H18: formula =ROUND(27500*per_Euro*USD_Change_IRR,-3) → base price is EUR (IRR value is only a conversion at per_Euro 1.085 × 420,000)
Note on AA24: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H18: EUR constant inside the formula
Note on AD24: نرخ پروژه: در فایل PEP-Rev.140205 گچساران ۴ (P.ME H18) قیمت با نرخ یورو 455,692 ریال (= ۴۲۰٬۰۰۰ ریال/دلار × ۱٫۰۸۵) برابر 12,531,523,563 ریال بوده است. این سلول با نرخ جدول FX بانک (سال ۱۴۰۲) محاسبه شده است.
Note on AF24: شرط تحویل: EXW (استنباطی). این قیمت = «هزینه واحد بدون ضریب» شیت P.ME سند PEP گچساران (Rev.1402/05). این قیمت شامل نیست (هر کدام سطر جداگانه دارند): حمل هر قلم (P.ME ستون N)، یدکی راه‌اندازی و دو ساله (Procurement D49)، بیمه ۱٪ (D51)، بارگیری و حمل ۳٪ (D52)، بازرسی شخص ثالث ۱٪ (D53)، خدمات فنی سازنده در نصب ۳٪ (D54)، بالاسری پروژه (EPC Summary، ستون «با اعمال سربار»)، نصب و مالیات.
Note on AO24: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AP24: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AQ24: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on E25: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F25: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G25: کلاس متریال در منبع ذکر نشده است.
Note on M25: PEP-Rev.140205 P.ME gives only flow / pressure / kW – no design standard stated (previous bank had "API 610 / IPS", unsupported)
Note on S25: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است (P.ME فقط توان kW را داده است)
Note on V25: INFERRED – source does not state pump type; "Centrifugal (assumed)" carried from previous bank
Note on W25: PEP P.ME: pressure given as "bar" – discharge / differential / design not specified
Note on Y25: INFERRED – PEP-Rev.140205 Gachsaran 4 PEP Rev.1402/05: IRR value is built with USD_Change_IRR = 420,000 ('basic data' B2 = 'Procurement' G1 'ارز مرجع'), i.e. the 1402 rate; base year of the EUR figure itself is not stated → 1402 assumed (previous bank had 1399 – not supported by the file)
Note on Z25: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H20: formula =ROUND(15000*per_Euro*USD_Change_IRR,-3) → base price is EUR (IRR value is only a conversion at per_Euro 1.085 × 420,000)
Note on AA25: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H20: EUR constant inside the formula
Note on AD25: نرخ پروژه: در فایل PEP-Rev.140205 گچساران ۴ (P.ME H20) قیمت با نرخ یورو 455,692 ریال (= ۴۲۰٬۰۰۰ ریال/دلار × ۱٫۰۸۵) برابر 6,835,376,489 ریال بوده است. این سلول با نرخ جدول FX بانک (سال ۱۴۰۲) محاسبه شده است.
Note on AF25: شرط تحویل: EXW (استنباطی). این قیمت = «هزینه واحد بدون ضریب» شیت P.ME سند PEP گچساران (Rev.1402/05). این قیمت شامل نیست (هر کدام سطر جداگانه دارند): حمل هر قلم (P.ME ستون N)، یدکی راه‌اندازی و دو ساله (Procurement D49)، بیمه ۱٪ (D51)، بارگیری و حمل ۳٪ (D52)، بازرسی شخص ثالث ۱٪ (D53)، خدمات فنی سازنده در نصب ۳٪ (D54)، بالاسری پروژه (EPC Summary، ستون «با اعمال سربار»)، نصب و مالیات.
Note on AO25: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AP25: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AQ25: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on E26: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F26: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G26: کلاس متریال در منبع ذکر نشده است.
Note on M26: PEP-Rev.140205 P.ME gives only flow / pressure / kW – no design standard stated (previous bank had "API 610 / IPS", unsupported)
Note on S26: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است (P.ME فقط توان kW را داده است)
Note on V26: INFERRED – source does not state pump type; "Centrifugal (assumed)" carried from previous bank
Note on W26: PEP P.ME: pressure given as "bar" – discharge / differential / design not specified
Note on Y26: INFERRED – PEP-Rev.140205 Gachsaran 4 PEP Rev.1402/05: IRR value is built with USD_Change_IRR = 420,000 ('basic data' B2 = 'Procurement' G1 'ارز مرجع'), i.e. the 1402 rate; base year of the EUR figure itself is not stated → 1402 assumed (previous bank had 1399 – not supported by the file)
Note on Z26: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H21: formula =ROUND(17000*per_Euro*USD_Change_IRR,-3) → base price is EUR (IRR value is only a conversion at per_Euro 1.085 × 420,000)
Note on AA26: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H21: EUR constant inside the formula
Note on AD26: نرخ پروژه: در فایل PEP-Rev.140205 گچساران ۴ (P.ME H21) قیمت با نرخ یورو 455,692 ریال (= ۴۲۰٬۰۰۰ ریال/دلار × ۱٫۰۸۵) برابر 7,746,760,021 ریال بوده است. این سلول با نرخ جدول FX بانک (سال ۱۴۰۲) محاسبه شده است.
Note on AF26: شرط تحویل: EXW (استنباطی). این قیمت = «هزینه واحد بدون ضریب» شیت P.ME سند PEP گچساران (Rev.1402/05). این قیمت شامل نیست (هر کدام سطر جداگانه دارند): حمل هر قلم (P.ME ستون N)، یدکی راه‌اندازی و دو ساله (Procurement D49)، بیمه ۱٪ (D51)، بارگیری و حمل ۳٪ (D52)، بازرسی شخص ثالث ۱٪ (D53)، خدمات فنی سازنده در نصب ۳٪ (D54)، بالاسری پروژه (EPC Summary، ستون «با اعمال سربار»)، نصب و مالیات.
Note on AO26: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AP26: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AQ26: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on E27: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F27: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G27: کلاس متریال در منبع ذکر نشده است.
Note on M27: PEP-Rev.140205 P.ME gives only flow / pressure / kW – no design standard stated (previous bank had "API 610 / IPS", unsupported)
Note on S27: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است (P.ME فقط توان kW را داده است)
Note on V27: INFERRED – source does not state pump type; "Centrifugal (assumed)" carried from previous bank
Note on W27: PEP P.ME: pressure given as "bar" – discharge / differential / design not specified
Note on Y27: INFERRED – PEP-Rev.140205 Gachsaran 4 PEP Rev.1402/05: IRR value is built with USD_Change_IRR = 420,000 ('basic data' B2 = 'Procurement' G1 'ارز مرجع'), i.e. the 1402 rate; base year of the EUR figure itself is not stated → 1402 assumed (previous bank had 1399 – not supported by the file)
Note on Z27: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H23: formula =ROUND(11000*per_Euro*USD_Change_IRR,-3) → base price is EUR (IRR value is only a conversion at per_Euro 1.085 × 420,000)
Note on AA27: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H23: EUR constant inside the formula
Note on AD27: نرخ پروژه: در فایل PEP-Rev.140205 گچساران ۴ (P.ME H23) قیمت با نرخ یورو 455,692 ریال (= ۴۲۰٬۰۰۰ ریال/دلار × ۱٫۰۸۵) برابر 5,012,609,000 ریال بوده است. این سلول با نرخ جدول FX بانک (سال ۱۴۰۲) محاسبه شده است.
Note on AF27: شرط تحویل: EXW (استنباطی). این قیمت = «هزینه واحد بدون ضریب» شیت P.ME سند PEP گچساران (Rev.1402/05). این قیمت شامل نیست (هر کدام سطر جداگانه دارند): حمل هر قلم (P.ME ستون N)، یدکی راه‌اندازی و دو ساله (Procurement D49)، بیمه ۱٪ (D51)، بارگیری و حمل ۳٪ (D52)، بازرسی شخص ثالث ۱٪ (D53)، خدمات فنی سازنده در نصب ۳٪ (D54)، بالاسری پروژه (EPC Summary، ستون «با اعمال سربار»)، نصب و مالیات.
Note on AO27: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AP27: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AQ27: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on E28: ROT-INJ = Produced Water & Disposal Injection Pumps آب تولیدی و پساب: Booster و پمپ‌های پرفشار تزریق به چاه دفعی
Note on F28: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G28: کلاس متریال در منبع ذکر نشده است.
Note on M28: PEP-Rev.140205 P.ME gives only flow / pressure / kW – no design standard stated (previous bank had "API 610 / IPS", unsupported)
Note on S28: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است (P.ME فقط توان kW را داده است)
Note on V28: INFERRED – source does not state pump type; "Centrifugal (assumed)" carried from previous bank
Note on W28: PEP P.ME: pressure given as "bar" – discharge / differential / design not specified
Note on Y28: INFERRED – PEP-Rev.140205 Gachsaran 4 PEP Rev.1402/05: IRR value is built with USD_Change_IRR = 420,000 ('basic data' B2 = 'Procurement' G1 'ارز مرجع'), i.e. the 1402 rate; base year of the EUR figure itself is not stated → 1402 assumed (previous bank had 1399 – not supported by the file)
Note on Z28: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H24: formula =ROUND(430000*per_Euro*USD_Change_IRR,-3) → base price is EUR (IRR value is only a conversion at per_Euro 1.085 × 420,000)
Note on AA28: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H24: EUR constant inside the formula
Note on AD28: نرخ پروژه: در فایل PEP-Rev.140205 گچساران ۴ (P.ME H24) قیمت با نرخ یورو 455,692 ریال (= ۴۲۰٬۰۰۰ ریال/دلار × ۱٫۰۸۵) برابر 195,947,459,000 ریال بوده است. این سلول با نرخ جدول FX بانک (سال ۱۴۰۲) محاسبه شده است.
Note on AF28: شرط تحویل: EXW (استنباطی). این قیمت = «هزینه واحد بدون ضریب» شیت P.ME سند PEP گچساران (Rev.1402/05). این قیمت شامل نیست (هر کدام سطر جداگانه دارند): حمل هر قلم (P.ME ستون N)، یدکی راه‌اندازی و دو ساله (Procurement D49)، بیمه ۱٪ (D51)، بارگیری و حمل ۳٪ (D52)، بازرسی شخص ثالث ۱٪ (D53)، خدمات فنی سازنده در نصب ۳٪ (D54)، بالاسری پروژه (EPC Summary، ستون «با اعمال سربار»)، نصب و مالیات.
Note on AO28: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AP28: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AQ28: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on E29: ROT-INJ = Produced Water & Disposal Injection Pumps آب تولیدی و پساب: Booster و پمپ‌های پرفشار تزریق به چاه دفعی
Note on F29: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G29: کلاس متریال در منبع ذکر نشده است.
Note on M29: PEP-Rev.140205 P.ME gives only flow / pressure / kW – no design standard stated (previous bank had "API 610 / IPS", unsupported)
Note on S29: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است (P.ME فقط توان kW را داده است)
Note on V29: INFERRED – source does not state pump type; "Centrifugal (assumed)" carried from previous bank
Note on W29: PEP P.ME: pressure given as "bar" – discharge / differential / design not specified
Note on Y29: INFERRED – PEP-Rev.140205 Gachsaran 4 PEP Rev.1402/05: IRR value is built with USD_Change_IRR = 420,000 ('basic data' B2 = 'Procurement' G1 'ارز مرجع'), i.e. the 1402 rate; base year of the EUR figure itself is not stated → 1402 assumed (previous bank had 1399 – not supported by the file)
Note on Z29: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H25: formula =ROUND(285000*per_Euro*USD_Change_IRR,-3) → base price is EUR (IRR value is only a conversion at per_Euro 1.085 × 420,000)
Note on AA29: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H25: EUR constant inside the formula
Note on AD29: نرخ پروژه: در فایل PEP-Rev.140205 گچساران ۴ (P.ME H25) قیمت با نرخ یورو 455,692 ریال (= ۴۲۰٬۰۰۰ ریال/دلار × ۱٫۰۸۵) برابر 129,872,153,000 ریال بوده است. این سلول با نرخ جدول FX بانک (سال ۱۴۰۲) محاسبه شده است.
Note on AF29: شرط تحویل: EXW (استنباطی). این قیمت = «هزینه واحد بدون ضریب» شیت P.ME سند PEP گچساران (Rev.1402/05). این قیمت شامل نیست (هر کدام سطر جداگانه دارند): حمل هر قلم (P.ME ستون N)، یدکی راه‌اندازی و دو ساله (Procurement D49)، بیمه ۱٪ (D51)، بارگیری و حمل ۳٪ (D52)، بازرسی شخص ثالث ۱٪ (D53)، خدمات فنی سازنده در نصب ۳٪ (D54)، بالاسری پروژه (EPC Summary، ستون «با اعمال سربار»)، نصب و مالیات.
Note on AO29: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AP29: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AQ29: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on E30: ROT-AUX = Chemical, Fuel & Auxiliary Pumps پمپ‌های جانبی: مواد شیمیایی، گلایکول، گازوئیل و سوخت — Reclassified 1405-07: ROT-INJ → ROT-AUX (service-based classification; approved)
Note on F30: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G30: کلاس متریال در منبع ذکر نشده است.
Note on M30: PEP-Rev.140205 P.ME gives only flow / pressure / kW – no design standard stated (previous bank had "API 610 / IPS", unsupported)
Note on S30: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است (P.ME فقط توان kW را داده است)
Note on V30: INFERRED – source does not state pump type; "Centrifugal (assumed)" carried from previous bank
Note on W30: PEP P.ME: pressure given as "bar" – discharge / differential / design not specified
Note on Y30: INFERRED – PEP-Rev.140205 Gachsaran 4 PEP Rev.1402/05: IRR value is built with USD_Change_IRR = 420,000 ('basic data' B2 = 'Procurement' G1 'ارز مرجع'), i.e. the 1402 rate; base year of the EUR figure itself is not stated → 1402 assumed (previous bank had 1399 – not supported by the file)
Note on Z30: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H36: formula =ROUND(9000*per_Euro*USD_Change_IRR,-3) → base price is EUR (IRR value is only a conversion at per_Euro 1.085 × 420,000)
Note on AA30: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H36: EUR constant inside the formula
Note on AD30: نرخ پروژه: در فایل PEP-Rev.140205 گچساران ۴ (P.ME H36) قیمت با نرخ یورو 455,692 ریال (= ۴۲۰٬۰۰۰ ریال/دلار × ۱٫۰۸۵) برابر 4,101,226,000 ریال بوده است. این سلول با نرخ جدول FX بانک (سال ۱۴۰۲) محاسبه شده است.
Note on AF30: شرط تحویل: EXW (استنباطی). این قیمت = «هزینه واحد بدون ضریب» شیت P.ME سند PEP گچساران (Rev.1402/05). این قیمت شامل نیست (هر کدام سطر جداگانه دارند): حمل هر قلم (P.ME ستون N)، یدکی راه‌اندازی و دو ساله (Procurement D49)، بیمه ۱٪ (D51)، بارگیری و حمل ۳٪ (D52)، بازرسی شخص ثالث ۱٪ (D53)، خدمات فنی سازنده در نصب ۳٪ (D54)، بالاسری پروژه (EPC Summary، ستون «با اعمال سربار»)، نصب و مالیات.
Note on AO30: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AP30: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AQ30: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on E31: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن
Note on F31: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G31: کلاس متریال در منبع ذکر نشده است.
Note on M31: PEP-Rev.140205 P.ME gives only flow / pressure / kW – no design standard stated (previous bank had "API 610 / IPS", unsupported)
Note on S31: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است (P.ME فقط توان kW را داده است)
Note on V31: INFERRED – source does not state pump type; "Centrifugal (assumed)" carried from previous bank
Note on W31: PEP P.ME: pressure given as "bar" – discharge / differential / design not specified
Note on Y31: INFERRED – PEP-Rev.140205 Gachsaran 4 PEP Rev.1402/05: IRR value is built with USD_Change_IRR = 420,000 ('basic data' B2 = 'Procurement' G1 'ارز مرجع'), i.e. the 1402 rate; base year of the EUR figure itself is not stated → 1402 assumed (previous bank had 1399 – not supported by the file)
Note on Z31: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H46: formula =ROUND(28000*per_Euro*USD_Change_IRR,-3) → base price is EUR (IRR value is only a conversion at per_Euro 1.085 × 420,000)
Note on AA31: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H46: EUR constant inside the formula
Note on AD31: نرخ پروژه: در فایل PEP-Rev.140205 گچساران ۴ (P.ME H46) قیمت با نرخ یورو 455,692 ریال (= ۴۲۰٬۰۰۰ ریال/دلار × ۱٫۰۸۵) برابر 12,759,369,000 ریال بوده است. این سلول با نرخ جدول FX بانک (سال ۱۴۰۲) محاسبه شده است.
Note on AF31: شرط تحویل: EXW (استنباطی). این قیمت = «هزینه واحد بدون ضریب» شیت P.ME سند PEP گچساران (Rev.1402/05). این قیمت شامل نیست (هر کدام سطر جداگانه دارند): حمل هر قلم (P.ME ستون N)، یدکی راه‌اندازی و دو ساله (Procurement D49)، بیمه ۱٪ (D51)، بارگیری و حمل ۳٪ (D52)، بازرسی شخص ثالث ۱٪ (D53)، خدمات فنی سازنده در نصب ۳٪ (D54)، بالاسری پروژه (EPC Summary، ستون «با اعمال سربار»)، نصب و مالیات.
Note on AO31: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AP31: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AQ31: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on E32: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن
Note on F32: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G32: کلاس متریال در منبع ذکر نشده است.
Note on M32: PEP-Rev.140205 P.ME gives only flow / pressure / kW – no design standard stated (previous bank had "API 610 / IPS", unsupported)
Note on S32: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است (P.ME فقط توان kW را داده است)
Note on V32: INFERRED – source does not state pump type; "Centrifugal (assumed)" carried from previous bank
Note on W32: PEP P.ME: pressure given as "bar" – discharge / differential / design not specified
Note on Y32: INFERRED – PEP-Rev.140205 Gachsaran 4 PEP Rev.1402/05: IRR value is built with USD_Change_IRR = 420,000 ('basic data' B2 = 'Procurement' G1 'ارز مرجع'), i.e. the 1402 rate; base year of the EUR figure itself is not stated → 1402 assumed (previous bank had 1399 – not supported by the file)
Note on Z32: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H50: formula =ROUND(53000*per_Euro*USD_Change_IRR,-3) → base price is EUR (IRR value is only a conversion at per_Euro 1.085 × 420,000)
Note on AA32: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H50: EUR constant inside the formula
Note on AD32: نرخ پروژه: در فایل PEP-Rev.140205 گچساران ۴ (P.ME H50) قیمت با نرخ یورو 455,692 ریال (= ۴۲۰٬۰۰۰ ریال/دلار × ۱٫۰۸۵) برابر 24,151,664,000 ریال بوده است. این سلول با نرخ جدول FX بانک (سال ۱۴۰۲) محاسبه شده است.
Note on AF32: شرط تحویل: EXW (استنباطی). این قیمت = «هزینه واحد بدون ضریب» شیت P.ME سند PEP گچساران (Rev.1402/05). این قیمت شامل نیست (هر کدام سطر جداگانه دارند): حمل هر قلم (P.ME ستون N)، یدکی راه‌اندازی و دو ساله (Procurement D49)، بیمه ۱٪ (D51)، بارگیری و حمل ۳٪ (D52)، بازرسی شخص ثالث ۱٪ (D53)، خدمات فنی سازنده در نصب ۳٪ (D54)، بالاسری پروژه (EPC Summary، ستون «با اعمال سربار»)، نصب و مالیات.
Note on AO32: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AP32: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AQ32: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on E33: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن
Note on F33: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G33: کلاس متریال در منبع ذکر نشده است.
Note on M33: PEP-Rev.140205 P.ME gives only flow / pressure / kW – no design standard stated (previous bank had "API 610 / IPS", unsupported)
Note on S33: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است (P.ME فقط توان kW را داده است)
Note on V33: INFERRED – source does not state pump type; "Centrifugal (assumed)" carried from previous bank
Note on W33: PEP P.ME: pressure given as "bar" – discharge / differential / design not specified
Note on Y33: INFERRED – PEP-Rev.140205 Gachsaran 4 PEP Rev.1402/05: IRR value is built with USD_Change_IRR = 420,000 ('basic data' B2 = 'Procurement' G1 'ارز مرجع'), i.e. the 1402 rate; base year of the EUR figure itself is not stated → 1402 assumed (previous bank had 1399 – not supported by the file)
Note on Z33: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H51: formula =ROUND(53000*per_Euro*USD_Change_IRR,-3) → base price is EUR (IRR value is only a conversion at per_Euro 1.085 × 420,000)
Note on AA33: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H51: EUR constant inside the formula
Note on AD33: نرخ پروژه: در فایل PEP-Rev.140205 گچساران ۴ (P.ME H51) قیمت با نرخ یورو 455,692 ریال (= ۴۲۰٬۰۰۰ ریال/دلار × ۱٫۰۸۵) برابر 24,151,664,000 ریال بوده است. این سلول با نرخ جدول FX بانک (سال ۱۴۰۲) محاسبه شده است.
Note on AF33: شرط تحویل: EXW (استنباطی). این قیمت = «هزینه واحد بدون ضریب» شیت P.ME سند PEP گچساران (Rev.1402/05). این قیمت شامل نیست (هر کدام سطر جداگانه دارند): حمل هر قلم (P.ME ستون N)، یدکی راه‌اندازی و دو ساله (Procurement D49)، بیمه ۱٪ (D51)، بارگیری و حمل ۳٪ (D52)، بازرسی شخص ثالث ۱٪ (D53)، خدمات فنی سازنده در نصب ۳٪ (D54)، بالاسری پروژه (EPC Summary، ستون «با اعمال سربار»)، نصب و مالیات.
Note on AO33: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AP33: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AQ33: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on E34: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F34: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G34: کلاس متریال در منبع ذکر نشده است.
Note on M34: PEP-Rev.140205 P.ME gives only flow / pressure / kW – no design standard stated (previous bank had "API 610 / IPS", unsupported)
Note on S34: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است (P.ME فقط توان kW را داده است)
Note on V34: INFERRED – source does not state pump type; "Centrifugal (assumed)" carried from previous bank
Note on W34: PEP P.ME: pressure given as "bar" – discharge / differential / design not specified
Note on Y34: INFERRED – PEP-Rev.140205 Gachsaran 4 PEP Rev.1402/05: IRR value is built with USD_Change_IRR = 420,000 ('basic data' B2 = 'Procurement' G1 'ارز مرجع'), i.e. the 1402 rate; base year of the EUR figure itself is not stated → 1402 assumed (previous bank had 1399 – not supported by the file)
Note on Z34: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H53: formula =ROUND(29000*per_Euro*USD_Change_IRR,-3) → base price is EUR (IRR value is only a conversion at per_Euro 1.085 × 420,000)
Note on AA34: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H53: EUR constant inside the formula
Note on AD34: نرخ پروژه: در فایل PEP-Rev.140205 گچساران ۴ (P.ME H53) قیمت با نرخ یورو 455,692 ریال (= ۴۲۰٬۰۰۰ ریال/دلار × ۱٫۰۸۵) برابر 13,215,061,000 ریال بوده است. این سلول با نرخ جدول FX بانک (سال ۱۴۰۲) محاسبه شده است.
Note on AF34: شرط تحویل: EXW (استنباطی). این قیمت = «هزینه واحد بدون ضریب» شیت P.ME سند PEP گچساران (Rev.1402/05). این قیمت شامل نیست (هر کدام سطر جداگانه دارند): حمل هر قلم (P.ME ستون N)، یدکی راه‌اندازی و دو ساله (Procurement D49)، بیمه ۱٪ (D51)، بارگیری و حمل ۳٪ (D52)، بازرسی شخص ثالث ۱٪ (D53)، خدمات فنی سازنده در نصب ۳٪ (D54)، بالاسری پروژه (EPC Summary، ستون «با اعمال سربار»)، نصب و مالیات.
Note on AO34: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AP34: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AQ34: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on E35: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن
Note on F35: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G35: کلاس متریال در منبع ذکر نشده است.
Note on M35: PEP-Rev.140205 P.ME gives only flow / pressure / kW – no design standard stated (previous bank had "API 610 / IPS", unsupported)
Note on S35: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است (P.ME فقط توان kW را داده است)
Note on V35: INFERRED – source does not state pump type; "Centrifugal (assumed)" carried from previous bank
Note on W35: PEP P.ME: pressure given as "bar" – discharge / differential / design not specified
Note on Y35: INFERRED – PEP-Rev.140205 Gachsaran 4 PEP Rev.1402/05: IRR value is built with USD_Change_IRR = 420,000 ('basic data' B2 = 'Procurement' G1 'ارز مرجع'), i.e. the 1402 rate; base year of the EUR figure itself is not stated → 1402 assumed (previous bank had 1399 – not supported by the file)
Note on Z35: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H54: formula =ROUND(35000*per_Euro*USD_Change_IRR,-3) → base price is EUR (IRR value is only a conversion at per_Euro 1.085 × 420,000)
Note on AA35: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H54: EUR constant inside the formula
Note on AD35: نرخ پروژه: در فایل PEP-Rev.140205 گچساران ۴ (P.ME H54) قیمت با نرخ یورو 455,692 ریال (= ۴۲۰٬۰۰۰ ریال/دلار × ۱٫۰۸۵) برابر 15,949,212,000 ریال بوده است. این سلول با نرخ جدول FX بانک (سال ۱۴۰۲) محاسبه شده است.
Note on AF35: شرط تحویل: EXW (استنباطی). این قیمت = «هزینه واحد بدون ضریب» شیت P.ME سند PEP گچساران (Rev.1402/05). این قیمت شامل نیست (هر کدام سطر جداگانه دارند): حمل هر قلم (P.ME ستون N)، یدکی راه‌اندازی و دو ساله (Procurement D49)، بیمه ۱٪ (D51)، بارگیری و حمل ۳٪ (D52)، بازرسی شخص ثالث ۱٪ (D53)، خدمات فنی سازنده در نصب ۳٪ (D54)، بالاسری پروژه (EPC Summary، ستون «با اعمال سربار»)، نصب و مالیات.
Note on AO35: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AP35: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AQ35: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on E36: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن
Note on F36: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G36: کلاس متریال در منبع ذکر نشده است.
Note on M36: PEP-Rev.140205 P.ME gives only flow / pressure / kW – no design standard stated (previous bank had "API 610 / IPS", unsupported)
Note on S36: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است (P.ME فقط توان kW را داده است)
Note on V36: INFERRED – source does not state pump type; "Centrifugal (assumed)" carried from previous bank
Note on W36: PEP P.ME: pressure given as "bar" – discharge / differential / design not specified
Note on Y36: INFERRED – PEP-Rev.140205 Gachsaran 4 PEP Rev.1402/05: IRR value is built with USD_Change_IRR = 420,000 ('basic data' B2 = 'Procurement' G1 'ارز مرجع'), i.e. the 1402 rate; base year of the EUR figure itself is not stated → 1402 assumed (previous bank had 1399 – not supported by the file)
Note on Z36: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H55: formula =ROUND(13350*per_Euro*USD_Change_IRR,-3) → base price is EUR (IRR value is only a conversion at per_Euro 1.085 × 420,000)
Note on AA36: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H55: EUR constant inside the formula
Note on AD36: نرخ پروژه: در فایل PEP-Rev.140205 گچساران ۴ (P.ME H55) قیمت با نرخ یورو 455,692 ریال (= ۴۲۰٬۰۰۰ ریال/دلار × ۱٫۰۸۵) برابر 6,083,485,000 ریال بوده است. این سلول با نرخ جدول FX بانک (سال ۱۴۰۲) محاسبه شده است.
Note on AF36: شرط تحویل: EXW (استنباطی). این قیمت = «هزینه واحد بدون ضریب» شیت P.ME سند PEP گچساران (Rev.1402/05). این قیمت شامل نیست (هر کدام سطر جداگانه دارند): حمل هر قلم (P.ME ستون N)، یدکی راه‌اندازی و دو ساله (Procurement D49)، بیمه ۱٪ (D51)، بارگیری و حمل ۳٪ (D52)، بازرسی شخص ثالث ۱٪ (D53)، خدمات فنی سازنده در نصب ۳٪ (D54)، بالاسری پروژه (EPC Summary، ستون «با اعمال سربار»)، نصب و مالیات.
Note on AO36: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AP36: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AQ36: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on E37: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن — Reclassified 1405-07: ROT-CRU → ROT-DRN (service-based classification; approved)
Note on F37: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G37: کلاس متریال در منبع ذکر نشده است.
Note on M37: PEP-Rev.140205 P.ME gives only flow / pressure / kW – no design standard stated (previous bank had "API 610 / IPS", unsupported)
Note on S37: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است (P.ME فقط توان kW را داده است)
Note on V37: INFERRED – source does not state pump type; "Centrifugal (assumed)" carried from previous bank
Note on W37: PEP P.ME: pressure given as "bar" – discharge / differential / design not specified
Note on Y37: INFERRED – PEP-Rev.140205 Gachsaran 4 PEP Rev.1402/05: IRR value is built with USD_Change_IRR = 420,000 ('basic data' B2 = 'Procurement' G1 'ارز مرجع'), i.e. the 1402 rate; base year of the EUR figure itself is not stated → 1402 assumed (previous bank had 1399 – not supported by the file)
Note on Z37: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H57: formula =ROUND(31000*per_Euro*USD_Change_IRR,-3) → base price is EUR (IRR value is only a conversion at per_Euro 1.085 × 420,000)
Note on AA37: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H57: EUR constant inside the formula
Note on AD37: نرخ پروژه: در فایل PEP-Rev.140205 گچساران ۴ (P.ME H57) قیمت با نرخ یورو 455,692 ریال (= ۴۲۰٬۰۰۰ ریال/دلار × ۱٫۰۸۵) برابر 14,126,445,000 ریال بوده است. این سلول با نرخ جدول FX بانک (سال ۱۴۰۲) محاسبه شده است.
Note on AF37: شرط تحویل: EXW (استنباطی). این قیمت = «هزینه واحد بدون ضریب» شیت P.ME سند PEP گچساران (Rev.1402/05). این قیمت شامل نیست (هر کدام سطر جداگانه دارند): حمل هر قلم (P.ME ستون N)، یدکی راه‌اندازی و دو ساله (Procurement D49)، بیمه ۱٪ (D51)، بارگیری و حمل ۳٪ (D52)، بازرسی شخص ثالث ۱٪ (D53)، خدمات فنی سازنده در نصب ۳٪ (D54)، بالاسری پروژه (EPC Summary، ستون «با اعمال سربار»)، نصب و مالیات.
Note on AO37: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AP37: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AQ37: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on E38: ROT-INJ = Produced Water & Disposal Injection Pumps آب تولیدی و پساب: Booster و پمپ‌های پرفشار تزریق به چاه دفعی
Note on F38: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G38: کلاس متریال در منبع ذکر نشده است.
Note on M38: PEP-Rev.140205 P.ME gives only flow / pressure / kW – no design standard stated (previous bank had "API 610 / IPS", unsupported)
Note on S38: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است (P.ME فقط توان kW را داده است)
Note on V38: INFERRED – source does not state pump type; "Centrifugal (assumed)" carried from previous bank
Note on W38: PEP P.ME: pressure given as "bar" – discharge / differential / design not specified
Note on Y38: INFERRED – PEP-Rev.140205 Gachsaran 4 PEP Rev.1402/05: IRR value is built with USD_Change_IRR = 420,000 ('basic data' B2 = 'Procurement' G1 'ارز مرجع'), i.e. the 1402 rate; base year of the EUR figure itself is not stated → 1402 assumed (previous bank had 1399 – not supported by the file)
Note on Z38: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H58: formula =ROUND(28000*per_Euro*USD_Change_IRR,-3) → base price is EUR (IRR value is only a conversion at per_Euro 1.085 × 420,000)
Note on AA38: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H58: EUR constant inside the formula
Note on AD38: نرخ پروژه: در فایل PEP-Rev.140205 گچساران ۴ (P.ME H58) قیمت با نرخ یورو 455,692 ریال (= ۴۲۰٬۰۰۰ ریال/دلار × ۱٫۰۸۵) برابر 12,759,369,000 ریال بوده است. این سلول با نرخ جدول FX بانک (سال ۱۴۰۲) محاسبه شده است.
Note on AF38: شرط تحویل: EXW (استنباطی). این قیمت = «هزینه واحد بدون ضریب» شیت P.ME سند PEP گچساران (Rev.1402/05). این قیمت شامل نیست (هر کدام سطر جداگانه دارند): حمل هر قلم (P.ME ستون N)، یدکی راه‌اندازی و دو ساله (Procurement D49)، بیمه ۱٪ (D51)، بارگیری و حمل ۳٪ (D52)، بازرسی شخص ثالث ۱٪ (D53)، خدمات فنی سازنده در نصب ۳٪ (D54)، بالاسری پروژه (EPC Summary، ستون «با اعمال سربار»)، نصب و مالیات.
Note on AO38: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AP38: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AQ38: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on E39: ROT-AUX = Chemical, Fuel & Auxiliary Pumps پمپ‌های جانبی: مواد شیمیایی، گلایکول، گازوئیل و سوخت
Note on F39: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G39: کلاس متریال در منبع ذکر نشده است.
Note on M39: PEP-Rev.140205 P.ME gives only flow / pressure / kW – no design standard stated (previous bank had "API 610 / IPS", unsupported)
Note on S39: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است (P.ME فقط توان kW را داده است) (P-801 پمپ گازوئیل است، نه پمپ دیزلی؛ مقدار قبلی Diesel Engine اشتباه بود)
Note on V39: INFERRED – source does not state pump type; "Centrifugal (assumed)" carried from previous bank
Note on W39: PEP P.ME: pressure given as "bar" – discharge / differential / design not specified
Note on Y39: INFERRED – PEP-Rev.140205 Gachsaran 4 PEP Rev.1402/05: IRR value is built with USD_Change_IRR = 420,000 ('basic data' B2 = 'Procurement' G1 'ارز مرجع'), i.e. the 1402 rate; base year of the EUR figure itself is not stated → 1402 assumed (previous bank had 1399 – not supported by the file)
Note on Z39: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H60: formula =ROUND(13500*per_Euro*USD_Change_IRR,-3) → base price is EUR (IRR value is only a conversion at per_Euro 1.085 × 420,000)
Note on AA39: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H60: EUR constant inside the formula
Note on AD39: نرخ پروژه: در فایل PEP-Rev.140205 گچساران ۴ (P.ME H60) قیمت با نرخ یورو 455,692 ریال (= ۴۲۰٬۰۰۰ ریال/دلار × ۱٫۰۸۵) برابر 6,151,839,000 ریال بوده است. این سلول با نرخ جدول FX بانک (سال ۱۴۰۲) محاسبه شده است.
Note on AF39: شرط تحویل: EXW (استنباطی). این قیمت = «هزینه واحد بدون ضریب» شیت P.ME سند PEP گچساران (Rev.1402/05). این قیمت شامل نیست (هر کدام سطر جداگانه دارند): حمل هر قلم (P.ME ستون N)، یدکی راه‌اندازی و دو ساله (Procurement D49)، بیمه ۱٪ (D51)، بارگیری و حمل ۳٪ (D52)، بازرسی شخص ثالث ۱٪ (D53)، خدمات فنی سازنده در نصب ۳٪ (D54)، بالاسری پروژه (EPC Summary، ستون «با اعمال سربار»)، نصب و مالیات.
Note on AO39: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AP39: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AQ39: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on E40: ROT-FIR = Firewater & Safety Pumps آتش‌نشانی: پمپ اصلی برقی و دیزلی، Jockey و بارگیری آب آتش‌نشانی
Note on F40: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G40: کلاس متریال در منبع ذکر نشده است.
Note on M40: PEP-Rev.140205 P.ME gives only flow / pressure / kW – no design standard stated (previous bank had "API 610 / IPS", unsupported)
Note on S40: SOURCE – equipment name states electric motor driven
Note on V40: INFERRED – source does not state pump type; "Centrifugal (assumed)" carried from previous bank
Note on W40: PEP P.ME: pressure given as "bar" – discharge / differential / design not specified
Note on Y40: INFERRED – PEP-Rev.140205 Gachsaran 4 P.ME H61: IRR constant (no formula) in PEP Rev.1402/05 → 1402 assumed (previous bank had 1399 – not supported by the file)
Note on AF40: شرط تحویل: EXW (استنباطی). این قیمت = «هزینه واحد بدون ضریب» شیت P.ME سند PEP گچساران (Rev.1402/05). این قیمت شامل نیست (هر کدام سطر جداگانه دارند): حمل هر قلم (P.ME ستون N)، یدکی راه‌اندازی و دو ساله (Procurement D49)، بیمه ۱٪ (D51)، بارگیری و حمل ۳٪ (D52)، بازرسی شخص ثالث ۱٪ (D53)، خدمات فنی سازنده در نصب ۳٪ (D54)، بالاسری پروژه (EPC Summary، ستون «با اعمال سربار»)، نصب و مالیات.
Note on AO40: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AP40: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AQ40: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on E41: ROT-FIR = Firewater & Safety Pumps آتش‌نشانی: پمپ اصلی برقی و دیزلی، Jockey و بارگیری آب آتش‌نشانی
Note on F41: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G41: کلاس متریال در منبع ذکر نشده است.
Note on M41: PEP-Rev.140205 P.ME gives only flow / pressure / kW – no design standard stated (previous bank had "API 610 / IPS", unsupported)
Note on S41: SOURCE – equipment name states diesel engine driven
Note on V41: INFERRED – source does not state pump type; "Centrifugal (assumed)" carried from previous bank
Note on W41: PEP P.ME: pressure given as "bar" – discharge / differential / design not specified
Note on Y41: INFERRED – PEP-Rev.140205 Gachsaran 4 P.ME H62: IRR constant (no formula) in PEP Rev.1402/05 → 1402 assumed (previous bank had 1399 – not supported by the file)
Note on AF41: شرط تحویل: EXW (استنباطی). این قیمت = «هزینه واحد بدون ضریب» شیت P.ME سند PEP گچساران (Rev.1402/05). این قیمت شامل نیست (هر کدام سطر جداگانه دارند): حمل هر قلم (P.ME ستون N)، یدکی راه‌اندازی و دو ساله (Procurement D49)، بیمه ۱٪ (D51)، بارگیری و حمل ۳٪ (D52)، بازرسی شخص ثالث ۱٪ (D53)، خدمات فنی سازنده در نصب ۳٪ (D54)، بالاسری پروژه (EPC Summary، ستون «با اعمال سربار»)، نصب و مالیات.
Note on AO41: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AP41: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AQ41: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on E42: ROT-FIR = Firewater & Safety Pumps آتش‌نشانی: پمپ اصلی برقی و دیزلی، Jockey و بارگیری آب آتش‌نشانی
Note on F42: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G42: کلاس متریال در منبع ذکر نشده است.
Note on M42: PEP-Rev.140205 P.ME gives only flow / pressure / kW – no design standard stated (previous bank had "API 610 / IPS", unsupported)
Note on S42: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است (P.ME فقط توان kW را داده است)
Note on V42: INFERRED – source does not state pump type; "Centrifugal (assumed)" carried from previous bank
Note on W42: PEP P.ME: pressure given as "bar" – discharge / differential / design not specified
Note on Y42: INFERRED – PEP-Rev.140205 Gachsaran 4 P.ME H63: IRR constant (no formula) in PEP Rev.1402/05 → 1402 assumed (previous bank had 1399 – not supported by the file)
Note on AF42: شرط تحویل: EXW (استنباطی). این قیمت = «هزینه واحد بدون ضریب» شیت P.ME سند PEP گچساران (Rev.1402/05). این قیمت شامل نیست (هر کدام سطر جداگانه دارند): حمل هر قلم (P.ME ستون N)، یدکی راه‌اندازی و دو ساله (Procurement D49)، بیمه ۱٪ (D51)، بارگیری و حمل ۳٪ (D52)، بازرسی شخص ثالث ۱٪ (D53)، خدمات فنی سازنده در نصب ۳٪ (D54)، بالاسری پروژه (EPC Summary، ستون «با اعمال سربار»)، نصب و مالیات.
Note on AO42: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AP42: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AQ42: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on E43: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F43: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G43: کلاس متریال در منبع ذکر نشده است.
Note on M43: PEP-Rev.140205 P.ME gives only flow / pressure / kW – no design standard stated (previous bank had "API 610 / IPS", unsupported)
Note on S43: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است (P.ME فقط توان kW را داده است)
Note on V43: INFERRED – source does not state pump type; "Centrifugal (assumed)" carried from previous bank
Note on W43: PEP P.ME: pressure given as "bar" – discharge / differential / design not specified
Note on Y43: INFERRED – PEP-Rev.140205 Gachsaran 4 PEP Rev.1402/05: IRR value is built with USD_Change_IRR = 420,000 ('basic data' B2 = 'Procurement' G1 'ارز مرجع'), i.e. the 1402 rate; base year of the EUR figure itself is not stated → 1402 assumed (previous bank had 1399 – not supported by the file)
Note on Z43: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H64: formula =ROUND(17500*per_Euro*USD_Change_IRR,-3) → base price is EUR (IRR value is only a conversion at per_Euro 1.085 × 420,000)
Note on AA43: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H64: EUR constant inside the formula
Note on AD43: نرخ پروژه: در فایل PEP-Rev.140205 گچساران ۴ (P.ME H64) قیمت با نرخ یورو 455,692 ریال (= ۴۲۰٬۰۰۰ ریال/دلار × ۱٫۰۸۵) برابر 7,974,606,000 ریال بوده است. این سلول با نرخ جدول FX بانک (سال ۱۴۰۲) محاسبه شده است.
Note on AF43: شرط تحویل: EXW (استنباطی). این قیمت = «هزینه واحد بدون ضریب» شیت P.ME سند PEP گچساران (Rev.1402/05). این قیمت شامل نیست (هر کدام سطر جداگانه دارند): حمل هر قلم (P.ME ستون N)، یدکی راه‌اندازی و دو ساله (Procurement D49)، بیمه ۱٪ (D51)، بارگیری و حمل ۳٪ (D52)، بازرسی شخص ثالث ۱٪ (D53)، خدمات فنی سازنده در نصب ۳٪ (D54)، بالاسری پروژه (EPC Summary، ستون «با اعمال سربار»)، نصب و مالیات.
Note on AO43: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AP43: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AQ43: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on E44: ROT-FIR = Firewater & Safety Pumps آتش‌نشانی: پمپ اصلی برقی و دیزلی، Jockey و بارگیری آب آتش‌نشانی
Note on F44: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G44: کلاس متریال در منبع ذکر نشده است.
Note on M44: PEP-Rev.140205 P.ME gives only flow / pressure / kW – no design standard stated (previous bank had "API 610 / IPS", unsupported)
Note on S44: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است (P.ME فقط توان kW را داده است)
Note on V44: INFERRED – source does not state pump type; "Centrifugal (assumed)" carried from previous bank
Note on W44: PEP P.ME: pressure given as "bar" – discharge / differential / design not specified
Note on Y44: INFERRED – PEP-Rev.140205 Gachsaran 4 PEP Rev.1402/05: IRR value is built with USD_Change_IRR = 420,000 ('basic data' B2 = 'Procurement' G1 'ارز مرجع'), i.e. the 1402 rate; base year of the EUR figure itself is not stated → 1402 assumed (previous bank had 1399 – not supported by the file)
Note on Z44: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H68: formula =ROUND(19500*per_Euro*USD_Change_IRR,-3) → base price is EUR (IRR value is only a conversion at per_Euro 1.085 × 420,000)
Note on AA44: SOURCE – PEP-Rev.140205 Gachsaran 4 P.ME H68: EUR constant inside the formula
Note on AD44: نرخ پروژه: در فایل PEP-Rev.140205 گچساران ۴ (P.ME H68) قیمت با نرخ یورو 455,692 ریال (= ۴۲۰٬۰۰۰ ریال/دلار × ۱٫۰۸۵) برابر 8,885,989,000 ریال بوده است. این سلول با نرخ جدول FX بانک (سال ۱۴۰۲) محاسبه شده است.
Note on AF44: شرط تحویل: EXW (استنباطی). این قیمت = «هزینه واحد بدون ضریب» شیت P.ME سند PEP گچساران (Rev.1402/05). این قیمت شامل نیست (هر کدام سطر جداگانه دارند): حمل هر قلم (P.ME ستون N)، یدکی راه‌اندازی و دو ساله (Procurement D49)، بیمه ۱٪ (D51)، بارگیری و حمل ۳٪ (D52)، بازرسی شخص ثالث ۱٪ (D53)، خدمات فنی سازنده در نصب ۳٪ (D54)، بالاسری پروژه (EPC Summary، ستون «با اعمال سربار»)، نصب و مالیات.
Note on AO44: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AP44: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on AQ44: INFERRED – PEP-Rev.140205 Gachsaran 4 'Procurement' rows 49–54: spares (commissioning + 2-yr) D49, insurance D51, transport D52, TPI D53 and vendor site services D54 are separate lines on top of the P.ME unit prices; P.ME column N (حمل) carries transport per item
Note on E45: ROT-CRU = Crude Oil & Main Transfer Pumps پمپ‌های نفت خام: انتقال نفت شور و نمک‌زدایی‌شده، Booster، Off-spec و انتقال اصلی
Note on F45: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G45: D-1: بدنه داپلکس، پروانه داپلکس؛ رینگ با روکش سخت؛ شفت داپلکس. کاربرد معمول: آب شور و آب تولیدی دارای کلراید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N45: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O45: INFERRED – KPL-476 R03 PUMPS-A (1) F19:F26: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S45: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y45: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF45: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ45: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E46: ROT-CRU = Crude Oil & Main Transfer Pumps پمپ‌های نفت خام: انتقال نفت شور و نمک‌زدایی‌شده، Booster، Off-spec و انتقال اصلی — Reclassified 1405-07: ROT-INJ → ROT-CRU (service-based classification; approved)
Note on F46: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G46: D-1: بدنه داپلکس، پروانه داپلکس؛ رینگ با روکش سخت؛ شفت داپلکس. کاربرد معمول: آب شور و آب تولیدی دارای کلراید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N46: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O46: INFERRED – KPL-476 R03 PUMPS-A (1) F27:F34: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S46: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y46: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF46: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ46: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E47: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن — Reclassified 1405-07: ROT-CRU → ROT-DRN (service-based classification; approved)
Note on F47: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G47: D-1: بدنه داپلکس، پروانه داپلکس؛ رینگ با روکش سخت؛ شفت داپلکس. کاربرد معمول: آب شور و آب تولیدی دارای کلراید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N47: SOURCE – design code line "& IPS-M-PM-140" in the project item description
Note on O47: INFERRED – KPL-476 R03 PUMPS-A (1) F35:F41: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S47: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y47: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF47: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ47: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E48: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F48: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G48: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N48: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O48: INFERRED – KPL-476 R03 PUMPS-A (1) F42:F49: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S48: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y48: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF48: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ48: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E49: ROT-INJ = Produced Water & Disposal Injection Pumps آب تولیدی و پساب: Booster و پمپ‌های پرفشار تزریق به چاه دفعی
Note on F49: BB3 – Between bearings, multistage, axially split: چندمرحله‌ای، بدنه دوتکه افقی؛ تزریق آب و انتقال پرفشار
Note on G49: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N49: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O49: INFERRED – KPL-476 R03 PUMPS-A (2) F19:F26: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S49: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y49: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF49: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ49: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E50: ROT-INJ = Produced Water & Disposal Injection Pumps آب تولیدی و پساب: Booster و پمپ‌های پرفشار تزریق به چاه دفعی
Note on F50: BB3 – Between bearings, multistage, axially split: چندمرحله‌ای، بدنه دوتکه افقی؛ تزریق آب و انتقال پرفشار
Note on G50: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N50: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O50: INFERRED – KPL-476 R03 PUMPS-A (2) F27:F34: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S50: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y50: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF50: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ50: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E51: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F51: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G51: S-5: بدنه فولاد کربنی، پروانه فولاد کربنی؛ رینگ کروم ۱۲٪ سخت‌شده؛ شفت AISI 4140. کاربرد معمول: هیدروکربن عمومی و داغ. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N51: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O51: INFERRED – KPL-476 R03 PUMPS-A (2) F35:F42: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S51: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y51: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF51: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ51: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E52: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F52: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G52: S-5: بدنه فولاد کربنی، پروانه فولاد کربنی؛ رینگ کروم ۱۲٪ سخت‌شده؛ شفت AISI 4140. کاربرد معمول: هیدروکربن عمومی و داغ. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N52: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O52: INFERRED – KPL-476 R03 PUMPS-A (2) F43:F50: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S52: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y52: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF52: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ52: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E53: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن
Note on F53: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G53: S-6: بدنه فولاد کربنی، پروانه کروم ۱۲٪؛ رینگ کروم ۱۲٪ سخت‌شده؛ شفت کروم ۱۲٪. کاربرد معمول: هیدروکربن داغ، آب ترش و خوردگی ملایم. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N53: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O53: INFERRED – KPL-476 R03 PUMPS-A (3) F19:F26: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S53: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y53: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF53: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ53: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E54: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن — Reclassified 1405-07: ROT-CRU → ROT-DRN (service-based classification; approved)
Note on F54: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G54: D-1: بدنه داپلکس، پروانه داپلکس؛ رینگ با روکش سخت؛ شفت داپلکس. کاربرد معمول: آب شور و آب تولیدی دارای کلراید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N54: SOURCE – design code line "& IPS-M-PM-140" in the project item description
Note on O54: INFERRED – KPL-476 R03 PUMPS-A (3) F27:F33: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S54: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y54: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF54: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ54: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E55: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F55: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G55: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N55: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O55: INFERRED – KPL-476 R03 PUMPS-A (3) F34:F41: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S55: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y55: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF55: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ55: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E56: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن
Note on F56: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G56: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N56: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O56: INFERRED – KPL-476 R03 PUMPS-A (3) F42:F49: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S56: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y56: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF56: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ56: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E57: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F57: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا — SOURCE – KPL-476 R03 DESALTERS-A F32
Note on G57: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G) — SOURCE – KPL-476 R03 DESALTERS-A F35
Note on H57: SOURCE – KPL-476 R03 DESALTERS-A F33: Pumps Rated Flow 21 m3/hr
Note on I57: INFERRED – KPL-476 R03 DESALTERS-A F34: Differential Pressure 4.4 barg → head ≈ 4.4×10.2 m (SG 1.0 assumed)
Note on N57: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O57: INFERRED – KPL-476 R03 DESALTERS-A F19:F37: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S57: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y57: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF57: قیمت جداگانه ندارد؛ این پمپ داخل قیمت پکیج آمده است (Remarks). شرط تحویل همان پکیج (FOB، با ضریب ×۱٫۵۸ جداگانه).
Note on E58: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F58: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا — SOURCE – KPL-476 R03 IWWTP-A (1) F32:F36
Note on G58: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G) — SOURCE – KPL-476 R03 IWWTP-A (1) F32:F36
Note on M58: SOURCE – KPL-476 R03 IWWTP-A (1) F32:F36
Note on N58: SOURCE – KPL-476 IWWTP-A (1) F35:F36: design code line "& IPS-G-PM-105"
Note on O58: INFERRED – KPL-476 R03 IWWTP-A (1) F32:F36: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S58: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on V58: SOURCE – KPL-476 R03 IWWTP-A (1) F32:F36
Note on Y58: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF58: قیمت جداگانه ندارد؛ این پمپ داخل قیمت پکیج آمده است (Remarks). شرط تحویل همان پکیج (FOB، با ضریب ×۱٫۵۸ جداگانه).
Note on E59: ROT-INJ = Produced Water & Disposal Injection Pumps آب تولیدی و پساب: Booster و پمپ‌های پرفشار تزریق به چاه دفعی
Note on F59: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا — SOURCE – KPL-476 R03 IWWTP-A (1) F37:F41
Note on G59: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G) — SOURCE – KPL-476 R03 IWWTP-A (1) F37:F41
Note on M59: SOURCE – KPL-476 R03 IWWTP-A (1) F37:F41
Note on N59: SOURCE – KPL-476 IWWTP-A (1) F40:F41: design code line "& IPS-G-PM-105"
Note on O59: INFERRED – KPL-476 R03 IWWTP-A (1) F37:F41: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S59: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on V59: SOURCE – KPL-476 R03 IWWTP-A (1) F37:F41
Note on Y59: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF59: قیمت جداگانه ندارد؛ این پمپ داخل قیمت پکیج آمده است (Remarks). شرط تحویل همان پکیج (FOB، با ضریب ×۱٫۵۸ جداگانه).
Note on E60: ROT-INJ = Produced Water & Disposal Injection Pumps آب تولیدی و پساب: Booster و پمپ‌های پرفشار تزریق به چاه دفعی
Note on F60: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا — SOURCE – KPL-476 R03 IWWTP-A (1) F37:F41
Note on G60: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G) — SOURCE – KPL-476 R03 IWWTP-A (1) F37:F41
Note on M60: SOURCE – KPL-476 R03 IWWTP-A (1) F37:F41
Note on N60: SOURCE – KPL-476 IWWTP-A (1) F40:F41: design code line "& IPS-G-PM-105"
Note on O60: INFERRED – KPL-476 R03 IWWTP-A (1) F37:F41: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S60: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on V60: SOURCE – KPL-476 R03 IWWTP-A (1) F37:F41
Note on Y60: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF60: قیمت جداگانه ندارد؛ این پمپ داخل قیمت پکیج آمده است (Remarks). شرط تحویل همان پکیج (FOB، با ضریب ×۱٫۵۸ جداگانه).
Note on E61: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن
Note on F61: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد — SOURCE – KPL-476 R03 IWWTP-A (1) F42:F46
Note on G61: D-1: بدنه داپلکس، پروانه داپلکس؛ رینگ با روکش سخت؛ شفت داپلکس. کاربرد معمول: آب شور و آب تولیدی دارای کلراید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G) — SOURCE – KPL-476 R03 IWWTP-A (1) F42:F46
Note on M61: SOURCE – KPL-476 R03 IWWTP-A (1) F42:F46
Note on N61: SOURCE – KPL-476 IWWTP-A (1) F45:F46: design code line "& IPS-M-PM-140"
Note on O61: INFERRED – KPL-476 R03 IWWTP-A (1) F42:F46: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S61: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on V61: SOURCE – KPL-476 R03 IWWTP-A (1) F42:F46
Note on Y61: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF61: قیمت جداگانه ندارد؛ این پمپ داخل قیمت پکیج آمده است (Remarks). شرط تحویل همان پکیج (FOB، با ضریب ×۱٫۵۸ جداگانه).
Note on E62: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن — Reclassified 1405-07: ROT-CRU → ROT-DRN (service-based classification; approved)
Note on F62: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد — SOURCE – KPL-476 R03 IWWTP-A (2) F16:F20
Note on G62: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G) — SOURCE – KPL-476 R03 IWWTP-A (2) F16:F20
Note on M62: SOURCE – KPL-476 R03 IWWTP-A (2) F16:F20 – NOTE: twin-screw pump stated as API 610 in source; API 676 expected – verify
Note on N62: SOURCE – KPL-476 IWWTP-A (2) F19:F20: design code line "& IPS-G-PM-105"
Note on O62: INFERRED – KPL-476 R03 IWWTP-A (2) F16:F20: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S62: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on V62: SOURCE – KPL-476 R03 IWWTP-A (2) F16:F20
Note on Y62: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF62: قیمت جداگانه ندارد؛ این پمپ داخل قیمت پکیج آمده است (Remarks). شرط تحویل همان پکیج (FOB، با ضریب ×۱٫۵۸ جداگانه).
Note on E63: ROT-CRU = Crude Oil & Main Transfer Pumps پمپ‌های نفت خام: انتقال نفت شور و نمک‌زدایی‌شده، Booster، Off-spec و انتقال اصلی
Note on F63: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G63: D-1: بدنه داپلکس، پروانه داپلکس؛ رینگ با روکش سخت؛ شفت داپلکس. کاربرد معمول: آب شور و آب تولیدی دارای کلراید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N63: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O63: SOURCE – KPL-476 R03 PUMPS-B F25: NACE 'MR-0175' Required: Yes
Note on S63: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y63: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF63: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ63: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E64: ROT-CRU = Crude Oil & Main Transfer Pumps پمپ‌های نفت خام: انتقال نفت شور و نمک‌زدایی‌شده، Booster، Off-spec و انتقال اصلی
Note on F64: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G64: D-1: بدنه داپلکس، پروانه داپلکس؛ رینگ با روکش سخت؛ شفت داپلکس. کاربرد معمول: آب شور و آب تولیدی دارای کلراید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N64: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O64: SOURCE – KPL-476 R03 PUMPS-B F34: NACE 'MR-0175' Required: Yes
Note on S64: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y64: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF64: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ64: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E65: ROT-CRU = Crude Oil & Main Transfer Pumps پمپ‌های نفت خام: انتقال نفت شور و نمک‌زدایی‌شده، Booster، Off-spec و انتقال اصلی — Reclassified 1405-07: ROT-INJ → ROT-CRU (service-based classification; approved)
Note on F65: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G65: D-1: بدنه داپلکس، پروانه داپلکس؛ رینگ با روکش سخت؛ شفت داپلکس. کاربرد معمول: آب شور و آب تولیدی دارای کلراید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N65: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O65: SOURCE – KPL-476 R03 PUMPS-B F43: NACE 'MR-0175' Required: Yes
Note on S65: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y65: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF65: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ65: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E66: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن — Reclassified 1405-07: ROT-CRU → ROT-DRN (service-based classification; approved)
Note on F66: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G66: D-1: بدنه داپلکس، پروانه داپلکس؛ رینگ با روکش سخت؛ شفت داپلکس. کاربرد معمول: آب شور و آب تولیدی دارای کلراید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N66: SOURCE – design code line "& IPS-M-PM-140" in the project item description
Note on O66: SOURCE – KPL-476 R03 PUMPS-B (2) F24: NACE 'MR-0175' Required: Yes
Note on S66: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y66: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF66: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ66: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E67: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F67: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G67: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N67: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O67: SOURCE – KPL-476 R03 PUMPS-B (2) F33: NACE 'MR-0175' Required: Yes
Note on S67: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y67: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF67: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ67: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E68: ROT-INJ = Produced Water & Disposal Injection Pumps آب تولیدی و پساب: Booster و پمپ‌های پرفشار تزریق به چاه دفعی
Note on F68: BB3 – Between bearings, multistage, axially split: چندمرحله‌ای، بدنه دوتکه افقی؛ تزریق آب و انتقال پرفشار
Note on G68: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N68: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O68: SOURCE – KPL-476 R03 PUMPS-B (2) F42: NACE 'MR-0175' Required: Yes
Note on S68: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y68: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF68: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ68: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E69: ROT-INJ = Produced Water & Disposal Injection Pumps آب تولیدی و پساب: Booster و پمپ‌های پرفشار تزریق به چاه دفعی
Note on F69: BB3 – Between bearings, multistage, axially split: چندمرحله‌ای، بدنه دوتکه افقی؛ تزریق آب و انتقال پرفشار
Note on G69: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N69: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O69: SOURCE – KPL-476 R03 PUMPS-B (3) F25: NACE 'MR-0175' Required: Yes
Note on S69: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y69: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF69: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ69: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E70: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F70: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G70: S-5: بدنه فولاد کربنی، پروانه فولاد کربنی؛ رینگ کروم ۱۲٪ سخت‌شده؛ شفت AISI 4140. کاربرد معمول: هیدروکربن عمومی و داغ. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N70: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O70: INFERRED – KPL-476 R03 PUMPS-B (3) F28:F35: no "NACE MR-0175 Required" line in item description, while the document states it item-by-item where required → N
Note on S70: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y70: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF70: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ70: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E71: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F71: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G71: S-5: بدنه فولاد کربنی، پروانه فولاد کربنی؛ رینگ کروم ۱۲٪ سخت‌شده؛ شفت AISI 4140. کاربرد معمول: هیدروکربن عمومی و داغ. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N71: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O71: INFERRED – KPL-476 R03 PUMPS-B (3) F36:F43: no "NACE MR-0175 Required" line in item description, while the document states it item-by-item where required → N
Note on S71: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y71: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF71: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ71: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E72: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن
Note on F72: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G72: S-6: بدنه فولاد کربنی، پروانه کروم ۱۲٪؛ رینگ کروم ۱۲٪ سخت‌شده؛ شفت کروم ۱۲٪. کاربرد معمول: هیدروکربن داغ، آب ترش و خوردگی ملایم. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N72: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O72: INFERRED – KPL-476 R03 PUMPS-B (4) F19:F26: no "NACE MR-0175 Required" line in item description, while the document states it item-by-item where required → N
Note on S72: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y72: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF72: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ72: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E73: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن — Reclassified 1405-07: ROT-CRU → ROT-DRN (service-based classification; approved)
Note on F73: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G73: D-1: بدنه داپلکس، پروانه داپلکس؛ رینگ با روکش سخت؛ شفت داپلکس. کاربرد معمول: آب شور و آب تولیدی دارای کلراید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N73: SOURCE – design code line "& IPS-M-PM-140" in the project item description
Note on O73: SOURCE – KPL-476 R03 PUMPS-B (4) F32: NACE 'MR-0175' Required: Yes
Note on S73: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y73: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF73: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ73: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E74: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F74: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G74: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N74: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O74: SOURCE – KPL-476 R03 PUMPS-B (4) F41: NACE 'MR-0175' Required: Yes
Note on S74: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y74: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF74: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ74: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E75: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن
Note on F75: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G75: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N75: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O75: SOURCE – KPL-476 R03 PUMPS-B (5) F25: NACE 'MR-0175' Required: Yes
Note on S75: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y75: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF75: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ75: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E76: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F76: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا — SOURCE – KPL-476 R03 DESALTERS-B F33
Note on G76: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G) — SOURCE – KPL-476 R03 DESALTERS-B F36
Note on H76: SOURCE – KPL-476 R03 DESALTERS-B F34: Pumps Rated Flow 15 m3/hr
Note on I76: INFERRED – KPL-476 R03 DESALTERS-B F35: Differential Pressure 4.4 barg → head ≈ 4.4×10.2 m (SG 1.0 assumed)
Note on N76: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O76: SOURCE – KPL-476 R03 DESALTERS-B F37: NACE 'MR-0175' Required: Yes
Note on S76: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y76: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF76: قیمت جداگانه ندارد؛ این پمپ داخل قیمت پکیج آمده است (Remarks). شرط تحویل همان پکیج (FOB، با ضریب ×۱٫۵۸ جداگانه).
Note on E77: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F77: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا — SOURCE – KPL-476 R03 IWWTP-B (1) F32:F36
Note on G77: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G) — SOURCE – KPL-476 R03 IWWTP-B (1) F32:F36
Note on M77: SOURCE – KPL-476 R03 IWWTP-B (1) F32:F36
Note on N77: SOURCE – KPL-476 IWWTP-B (1) F35:F36: design code line "& IPS-G-PM-105"
Note on O77: INFERRED – KPL-476 R03 IWWTP-B (1) F32:F36: no "NACE MR-0175 Required" line in item description, while the document states it item-by-item where required → N
Note on S77: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on V77: SOURCE – KPL-476 R03 IWWTP-B (1) F32:F36
Note on Y77: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF77: قیمت جداگانه ندارد؛ این پمپ داخل قیمت پکیج آمده است (Remarks). شرط تحویل همان پکیج (FOB، با ضریب ×۱٫۵۸ جداگانه).
Note on E78: ROT-INJ = Produced Water & Disposal Injection Pumps آب تولیدی و پساب: Booster و پمپ‌های پرفشار تزریق به چاه دفعی
Note on F78: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا — SOURCE – KPL-476 R03 IWWTP-B (1) F37:F42
Note on G78: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G) — SOURCE – KPL-476 R03 IWWTP-B (1) F37:F42
Note on M78: SOURCE – KPL-476 R03 IWWTP-B (1) F37:F42
Note on N78: SOURCE – KPL-476 IWWTP-B (1) F41:F42: design code line "& IPS-G-PM-105"
Note on O78: SOURCE – KPL-476 R03 IWWTP-B (1) F37:F42: NACE 'MR-0175' Required: Yes
Note on S78: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on V78: SOURCE – KPL-476 R03 IWWTP-B (1) F37:F42
Note on Y78: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF78: قیمت جداگانه ندارد؛ این پمپ داخل قیمت پکیج آمده است (Remarks). شرط تحویل همان پکیج (FOB، با ضریب ×۱٫۵۸ جداگانه).
Note on E79: ROT-INJ = Produced Water & Disposal Injection Pumps آب تولیدی و پساب: Booster و پمپ‌های پرفشار تزریق به چاه دفعی
Note on F79: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا — SOURCE – KPL-476 R03 IWWTP-B (1) F37:F42
Note on G79: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G) — SOURCE – KPL-476 R03 IWWTP-B (1) F37:F42
Note on M79: SOURCE – KPL-476 R03 IWWTP-B (1) F37:F42
Note on N79: SOURCE – KPL-476 IWWTP-B (1) F41:F42: design code line "& IPS-G-PM-105"
Note on O79: SOURCE – KPL-476 R03 IWWTP-B (1) F37:F42: NACE 'MR-0175' Required: Yes
Note on S79: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on V79: SOURCE – KPL-476 R03 IWWTP-B (1) F37:F42
Note on Y79: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF79: قیمت جداگانه ندارد؛ این پمپ داخل قیمت پکیج آمده است (Remarks). شرط تحویل همان پکیج (FOB، با ضریب ×۱٫۵۸ جداگانه).
Note on E80: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن
Note on F80: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد — SOURCE – KPL-476 R03 IWWTP-B (1) F43:F47
Note on G80: D-1: بدنه داپلکس، پروانه داپلکس؛ رینگ با روکش سخت؛ شفت داپلکس. کاربرد معمول: آب شور و آب تولیدی دارای کلراید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G) — SOURCE – KPL-476 R03 IWWTP-B (1) F43:F47
Note on M80: SOURCE – KPL-476 R03 IWWTP-B (1) F43:F47
Note on N80: SOURCE – KPL-476 IWWTP-B (1) F46:F47: design code line "& IPS-M-PM-140"
Note on O80: INFERRED – KPL-476 R03 IWWTP-B (1) F43:F47: no "NACE MR-0175 Required" line in item description, while the document states it item-by-item where required → N
Note on S80: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on V80: SOURCE – KPL-476 R03 IWWTP-B (1) F43:F47
Note on Y80: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF80: قیمت جداگانه ندارد؛ این پمپ داخل قیمت پکیج آمده است (Remarks). شرط تحویل همان پکیج (FOB، با ضریب ×۱٫۵۸ جداگانه).
Note on E81: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن — Reclassified 1405-07: ROT-CRU → ROT-DRN (service-based classification; approved)
Note on F81: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد — SOURCE – KPL-476 R03 IWWTP-B (2) F17:F21
Note on G81: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G) — SOURCE – KPL-476 R03 IWWTP-B (2) F17:F21
Note on M81: SOURCE – KPL-476 R03 IWWTP-B (2) F17:F21 – NOTE: twin-screw pump stated as API 610 in source; API 676 expected – verify
Note on N81: SOURCE – KPL-476 IWWTP-B (2) F20:F21: design code line "& IPS-G-PM-105"
Note on O81: SOURCE – KPL-476 R03 IWWTP-B (2) F17:F21: NACE 'MR-0175' Required: Yes
Note on S81: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on V81: SOURCE – KPL-476 R03 IWWTP-B (2) F17:F21
Note on Y81: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF81: قیمت جداگانه ندارد؛ این پمپ داخل قیمت پکیج آمده است (Remarks). شرط تحویل همان پکیج (FOB، با ضریب ×۱٫۵۸ جداگانه).
Note on E82: ROT-INJ = Produced Water & Disposal Injection Pumps آب تولیدی و پساب: Booster و پمپ‌های پرفشار تزریق به چاه دفعی
Note on F82: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا — SOURCE – KPL-476 R03 STRIPPER-B F36
Note on G82: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G) — SOURCE – KPL-476 R03 STRIPPER-B F39
Note on H82: SOURCE – KPL-476 R03 STRIPPER-B F37: Pumps Rated Flow 50 m3/hr
Note on I82: INFERRED – KPL-476 R03 STRIPPER-B F38: Differential Pressure 3 barg → head ≈ 3×10.2 m (SG 1.0 assumed)
Note on N82: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O82: INFERRED – KPL-476 R03 STRIPPER-B F34:F41: no "NACE MR-0175 Required" line in item description, while the document states it item-by-item where required → N
Note on S82: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y82: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF82: قیمت جداگانه ندارد؛ این پمپ داخل قیمت پکیج آمده است (Remarks). شرط تحویل همان پکیج (FOB، با ضریب ×۱٫۵۸ جداگانه).
Note on E83: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F83: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G83: I-2: بدنه چدن، پروانه برنز؛ رینگ برنز؛ شفت فولاد کربنی. کاربرد معمول: آب، آب آتش‌نشانی و آب شیرین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N83: SOURCE – design code line "& IPS-M-PM-115" in the project item description
Note on O83: INFERRED – KPL-476 R03 PUMPS-C F19:F26: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S83: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y83: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF83: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ83: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E84: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F84: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G84: I-2: بدنه چدن، پروانه برنز؛ رینگ برنز؛ شفت فولاد کربنی. کاربرد معمول: آب، آب آتش‌نشانی و آب شیرین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N84: SOURCE – design code line "& IPS-M-PM-115" in the project item description
Note on O84: INFERRED – KPL-476 R03 PUMPS-C F27:F34: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S84: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y84: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF84: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ84: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E85: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن
Note on F85: VS4 – Vertically suspended, line-shaft, separate discharge (sump): پمپ عمودی Sump با شفت بلند و لوله خروجی جدا؛ چاهک درین و Flare KO
Note on G85: S-6: بدنه فولاد کربنی، پروانه کروم ۱۲٪؛ رینگ کروم ۱۲٪ سخت‌شده؛ شفت کروم ۱۲٪. کاربرد معمول: هیدروکربن داغ، آب ترش و خوردگی ملایم. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N85: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O85: INFERRED – KPL-476 R03 PUMPS-C F35:F42: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S85: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y85: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF85: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ85: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E86: ROT-AUX = Chemical, Fuel & Auxiliary Pumps پمپ‌های جانبی: مواد شیمیایی، گلایکول، گازوئیل و سوخت
Note on F86: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G86: S-1: بدنه فولاد کربنی، پروانه چدن؛ رینگ چدن؛ شفت فولاد کربنی. کاربرد معمول: هیدروکربن غیرخورنده. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N86: SOURCE – design code line "& IPS-M-PM-115" in the project item description
Note on O86: INFERRED – KPL-476 R03 PUMPS-C F43:F50: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S86: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y86: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF86: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ86: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E87: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن
Note on F87: VS4 – Vertically suspended, line-shaft, separate discharge (sump): پمپ عمودی Sump با شفت بلند و لوله خروجی جدا؛ چاهک درین و Flare KO
Note on G87: S-6: بدنه فولاد کربنی، پروانه کروم ۱۲٪؛ رینگ کروم ۱۲٪ سخت‌شده؛ شفت کروم ۱۲٪. کاربرد معمول: هیدروکربن داغ، آب ترش و خوردگی ملایم. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N87: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O87: INFERRED – KPL-476 R03 PUMPS-C (2) F19:F26: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S87: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y87: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF87: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ87: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E88: ROT-FIR = Firewater & Safety Pumps آتش‌نشانی: پمپ اصلی برقی و دیزلی، Jockey و بارگیری آب آتش‌نشانی
Note on F88: BB (unspecified) – Between bearings – subtype not stated: منبع فقط «Between Bearings» گفته و زیرنوع API را مشخص نکرده — SOURCE – KPL-476 PUMPS-C (2) F28:F29 / F37:F38: "Horizontal, Impeller Between Bearings Design"
Note on G88: I-2: بدنه چدن، پروانه برنز؛ رینگ برنز؛ شفت فولاد کربنی. کاربرد معمول: آب، آب آتش‌نشانی و آب شیرین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N88: SOURCE – design code line "& IPS-M-PM-125" in the project item description
Note on O88: INFERRED – KPL-476 R03 PUMPS-C (2) F27:F35: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S88: SOURCE – equipment name states electric motor driven
Note on Y88: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF88: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ88: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E89: ROT-FIR = Firewater & Safety Pumps آتش‌نشانی: پمپ اصلی برقی و دیزلی، Jockey و بارگیری آب آتش‌نشانی
Note on F89: BB (unspecified) – Between bearings – subtype not stated: منبع فقط «Between Bearings» گفته و زیرنوع API را مشخص نکرده — SOURCE – KPL-476 PUMPS-C (2) F28:F29 / F37:F38: "Horizontal, Impeller Between Bearings Design"
Note on G89: I-2: بدنه چدن، پروانه برنز؛ رینگ برنز؛ شفت فولاد کربنی. کاربرد معمول: آب، آب آتش‌نشانی و آب شیرین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N89: SOURCE – design code line "& IPS-M-PM-125" in the project item description
Note on O89: INFERRED – KPL-476 R03 PUMPS-C (2) F36:F44: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S89: SOURCE – equipment name states diesel engine driven
Note on Y89: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF89: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ89: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E90: ROT-FIR = Firewater & Safety Pumps آتش‌نشانی: پمپ اصلی برقی و دیزلی، Jockey و بارگیری آب آتش‌نشانی
Note on F90: OH (unspecified) – Overhung – subtype not stated: منبع فقط «Overhung» گفته و زیرنوع API را مشخص نکرده — SOURCE – KPL-476 PUMPS-C (3) F20:F21: "Horizontal, Overhung Impeller Design"
Note on G90: I-2: بدنه چدن، پروانه برنز؛ رینگ برنز؛ شفت فولاد کربنی. کاربرد معمول: آب، آب آتش‌نشانی و آب شیرین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N90: SOURCE – design code line "& IPS-M-PM-125" in the project item description
Note on O90: INFERRED – KPL-476 R03 PUMPS-C (3) F19:F27: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S90: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y90: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF90: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ90: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E91: ROT-FIR = Firewater & Safety Pumps آتش‌نشانی: پمپ اصلی برقی و دیزلی، Jockey و بارگیری آب آتش‌نشانی
Note on F91: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G91: I-2: بدنه چدن، پروانه برنز؛ رینگ برنز؛ شفت فولاد کربنی. کاربرد معمول: آب، آب آتش‌نشانی و آب شیرین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N91: SOURCE – design code line "& IPS-M-PM-115" in the project item description
Note on O91: INFERRED – KPL-476 R03 PUMPS-C (3) F28:F35: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S91: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y91: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF91: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ91: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E92: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F92: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G92: I-2: بدنه چدن، پروانه برنز؛ رینگ برنز؛ شفت فولاد کربنی. کاربرد معمول: آب، آب آتش‌نشانی و آب شیرین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on I92: INFERRED – KPL-476 R03 PUMPS-C (3) F46: Differential Pressure 3 bar → head ≈ 3×10.2 m (SG 1.0 assumed)
Note on N92: SOURCE – design code line "& IPS-M-PM-115" in the project item description
Note on O92: INFERRED – KPL-476 R03 PUMPS-C (3) F41:F49: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S92: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y92: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on Z92: SOURCE – KPL-476 R03 PUMPS-C (3) U41: value is in column "Unit Price (Rials)" – previous bank had EUR (error)
Note on AF92: شرط تحویل: EXW (استنباطی؛ خرید داخلی ریالی). این قیمت شامل: قیمت فروشنده داخلی. این قیمت شامل نیست (KPL-476، TOTAL (2) سلول A20 با ضریب ×۱٫۲۷): هزینه بانکی ۲٪، بیمه ۰٫۵٪، بازرسی و حمل ۲٫۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. نصب و مالیات هم شامل نیست.
Note on AQ92: INFERRED – KPL-476 R03 TOTAL (2) A20: inspection cost carried in overhead factor, not in vendor unit price
Note on E93: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F93: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G93: I-2: بدنه چدن، پروانه برنز؛ رینگ برنز؛ شفت فولاد کربنی. کاربرد معمول: آب، آب آتش‌نشانی و آب شیرین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on I93: INFERRED – KPL-476 R03 PUMPS-C (4) F23: Differential Pressure 3 bar → head ≈ 3×10.2 m (SG 1.0 assumed)
Note on N93: SOURCE – design code line "& IPS-M-PM-115" in the project item description
Note on O93: INFERRED – KPL-476 R03 PUMPS-C (4) F19:F26: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S93: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y93: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on Z93: SOURCE – KPL-476 R03 PUMPS-C (4) U19: value is in column "Unit Price (Rials)" – previous bank had EUR (error)
Note on AF93: شرط تحویل: EXW (استنباطی؛ خرید داخلی ریالی). این قیمت شامل: قیمت فروشنده داخلی. این قیمت شامل نیست (KPL-476، TOTAL (2) سلول A20 با ضریب ×۱٫۲۷): هزینه بانکی ۲٪، بیمه ۰٫۵٪، بازرسی و حمل ۲٫۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. نصب و مالیات هم شامل نیست.
Note on AQ93: INFERRED – KPL-476 R03 TOTAL (2) A20: inspection cost carried in overhead factor, not in vendor unit price
Note on E94: ROT-INJ = Produced Water & Disposal Injection Pumps آب تولیدی و پساب: Booster و پمپ‌های پرفشار تزریق به چاه دفعی
Note on F94: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G94: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on I94: INFERRED – KPL-476 R03 PUMPS-A (4) F24: Differential Pressure 2 barg → head ≈ 2×10.2 m (SG 1.0 assumed)
Note on O94: INFERRED – KPL-476 R03 PUMPS-A (4) F19:F26: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S94: SOURCE – KPL-476 R03 PUMPS-A (4) F21
Note on Y94: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF94: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ94: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E95: ROT-INJ = Produced Water & Disposal Injection Pumps آب تولیدی و پساب: Booster و پمپ‌های پرفشار تزریق به چاه دفعی
Note on F95: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G95: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on I95: INFERRED – KPL-476 R03 PUMPS-B (5) F33: Differential Pressure 2 barg → head ≈ 2×10.2 m (SG 1.0 assumed)
Note on O95: INFERRED – KPL-476 R03 PUMPS-B (5) F28:F35: no "NACE MR-0175 Required" line in item description, while the document states it item-by-item where required → N
Note on S95: SOURCE – KPL-476 R03 PUMPS-B (5) F30
Note on Y95: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on AF95: شرط تحویل: FOB (استنباطی). این قیمت شامل: قیمت فروشنده برای پمپ طبق قلم MTO. این قیمت شامل نیست (در گزارش KPL-476، شیت TOTAL (2) سلول A29 جداگانه با ضریب بالاسری ×۱٫۵۸ اضافه شده): هزینه بانکی ۲٪، بیمه ۰٫۴٪، بازرسی و حمل ۳٪، ترخیص گمرکی ۲۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. همچنین نصب (شیت‌های INS) و مالیات بر ارزش افزوده در این قیمت نیست.
Note on AQ95: INFERRED – KPL-476 R03 TOTAL (2) A29: inspection cost carried in overhead factor, not in vendor unit price
Note on E96: ROT-AUX = Chemical, Fuel & Auxiliary Pumps پمپ‌های جانبی: مواد شیمیایی، گلایکول، گازوئیل و سوخت — Reclassified 1405-07: ROT-INJ → ROT-AUX (service-based classification; approved)
Note on F96: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G96: SS316L (non-API): بدنه فولاد ضدزنگ 316L، پروانه فولاد ضدزنگ 316L؛ —. کاربرد معمول: ساخت غیر API (مثلاً پمپ بشکه‌ای پرتابل). (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on H96: SOURCE – KPL-476 R03 PUMPS-C (3) F38: Rated Flow 160 Lit/min = 9.6 m3/hr (previous bank had 160 m3/h – unit error)
Note on M96: Source item gives type / flow / material only – no design standard (previous bank "API 610 / IPS" unsupported; a portable barrel pump is not an API 610 pump)
Note on O96: INFERRED – KPL-476 R03 PUMPS-C (3) F36:F40: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S96: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y96: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on Z96: SOURCE – KPL-476 R03 PUMPS-C (3) U36: value is in column "Unit Price (Rials)" – previous bank had EUR (error)
Note on AF96: شرط تحویل: EXW (استنباطی؛ خرید داخلی ریالی). این قیمت شامل: قیمت فروشنده داخلی. این قیمت شامل نیست (KPL-476، TOTAL (2) سلول A20 با ضریب ×۱٫۲۷): هزینه بانکی ۲٪، بیمه ۰٫۵٪، بازرسی و حمل ۲٫۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. نصب و مالیات هم شامل نیست.
Note on AQ96: INFERRED – KPL-476 R03 TOTAL (2) A20: inspection cost carried in overhead factor, not in vendor unit price
Note on E97: ROT-AUX = Chemical, Fuel & Auxiliary Pumps پمپ‌های جانبی: مواد شیمیایی، گلایکول، گازوئیل و سوخت — Reclassified 1405-07: ROT-WAT → ROT-AUX (service-based classification; approved)
Note on F97: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G97: SS316L (non-API): بدنه فولاد ضدزنگ 316L، پروانه فولاد ضدزنگ 316L؛ —. کاربرد معمول: ساخت غیر API (مثلاً پمپ بشکه‌ای پرتابل). (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on M97: Source item gives type / flow / material only – no design standard (previous bank "API 610 / IPS" unsupported; a portable barrel pump is not an API 610 pump)
Note on O97: INFERRED – KPL-476 R03 PUMPS-C (4) F27:F31: no "NACE MR-0175" line anywhere in Asmari (-A) or Common (-C) sheets, while the document states it item-by-item for the Bangestan train (12 "-B" sheets) → N
Note on S97: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y97: INFERRED – سال قیمت در KPL-476 صریح نیست. Cover: R00 = JUN 2014 (۱۳۹۳)، R03 = JAN 2016 (دی ۱۳۹۴)؛ برآورد نصب بر پایه «فهرست بهای نفت سال ۹۳» (INS-PUMP) → ۱۳۹۳ فرض شد. اگر ۱۳۹۴ باشد اثر بر قیمت تعدیل‌شده حدود ۰٫۸٪ است.
Note on Z97: SOURCE – KPL-476 R03 PUMPS-C (4) U27: value is in column "Unit Price (Rials)" – previous bank had EUR (error)
Note on AF97: شرط تحویل: EXW (استنباطی؛ خرید داخلی ریالی). این قیمت شامل: قیمت فروشنده داخلی. این قیمت شامل نیست (KPL-476، TOTAL (2) سلول A20 با ضریب ×۱٫۲۷): هزینه بانکی ۲٪، بیمه ۰٫۵٪، بازرسی و حمل ۲٫۵٪، هزینه‌های دفتری ۰٫۵٪، سود پیمانکار ۱۰٪، عدم قطعیت طراحی پایه ۱۰٪. نصب و مالیات هم شامل نیست.
Note on AQ97: INFERRED – KPL-476 R03 TOTAL (2) A20: inspection cost carried in overhead factor, not in vendor unit price
Note on E98: ROT-CRU = Crude Oil & Main Transfer Pumps پمپ‌های نفت خام: انتقال نفت شور و نمک‌زدایی‌شده، Booster، Off-spec و انتقال اصلی
Note on F98: VS6 – Vertically suspended, double casing, diffuser (can): عمودی دوبدنه در قوطی (Can)؛ NPSH کم، مثل Off-spec و مایعات نزدیک نقطه جوش
Note on G98: D-1: بدنه داپلکس، پروانه داپلکس؛ رینگ با روکش سخت؛ شفت داپلکس. کاربرد معمول: آب شور و آب تولیدی دارای کلراید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N98: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O98: SOURCE – PC-ME 14040105 Pazanan2 PUMPS B8: NACE 'MR-0175' Required: Yes
Note on S98: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y98: SOURCE – PC-ME PUMPS F7: «GOING UNIT PRICE FOB EUR 1404Q1»
Note on AF98: شرط تحویل: FOB (صریح؛ سرستون F7 «GOING UNIT PRICE FOB EUR 1404Q1»). این قیمت = میانگین پیشنهادهای فروشندگان (Vendor_Quotes). این قیمت شامل نیست: ضریب سربار تأمین کالا ×۱٫۱۸ و مالیات بر ارزش افزوده ۱۰٪ (PUMPS G30:H31)، حمل از بندر، بیمه، ترخیص و نصب. شمول یدکی و TPI در پیشنهادها مشخص نیست.
Note on E99: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F99: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G99: I-2: بدنه چدن، پروانه برنز؛ رینگ برنز؛ شفت فولاد کربنی. کاربرد معمول: آب، آب آتش‌نشانی و آب شیرین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N99: SOURCE – design code line "& IPS-M-PM-115" in the project item description
Note on O99: INFERRED – PC-ME 14040105 Pazanan2 PUMPS B9: no "NACE MR-0175" line in item description, while the document states it item-by-item where required → N
Note on S99: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y99: SOURCE – PC-ME PUMPS F7: «GOING UNIT PRICE FOB EUR 1404Q1»
Note on AF99: شرط تحویل: FOB (صریح؛ سرستون F7 «GOING UNIT PRICE FOB EUR 1404Q1»). این قیمت = میانگین پیشنهادهای فروشندگان (Vendor_Quotes). این قیمت شامل نیست: ضریب سربار تأمین کالا ×۱٫۱۸ و مالیات بر ارزش افزوده ۱۰٪ (PUMPS G30:H31)، حمل از بندر، بیمه، ترخیص و نصب. شمول یدکی و TPI در پیشنهادها مشخص نیست.
Note on E100: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F100: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G100: I-2: بدنه چدن، پروانه برنز؛ رینگ برنز؛ شفت فولاد کربنی. کاربرد معمول: آب، آب آتش‌نشانی و آب شیرین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N100: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O100: INFERRED – PC-ME 14040105 Pazanan2 PUMPS B10: no "NACE MR-0175" line in item description, while the document states it item-by-item where required → N
Note on S100: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y100: SOURCE – PC-ME PUMPS F7: «GOING UNIT PRICE FOB EUR 1404Q1»
Note on AF100: شرط تحویل: FOB (صریح؛ سرستون F7 «GOING UNIT PRICE FOB EUR 1404Q1»). این قیمت = میانگین پیشنهادهای فروشندگان (Vendor_Quotes). این قیمت شامل نیست: ضریب سربار تأمین کالا ×۱٫۱۸ و مالیات بر ارزش افزوده ۱۰٪ (PUMPS G30:H31)، حمل از بندر، بیمه، ترخیص و نصب. شمول یدکی و TPI در پیشنهادها مشخص نیست.
Note on E101: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F101: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G101: I-2: بدنه چدن، پروانه برنز؛ رینگ برنز؛ شفت فولاد کربنی. کاربرد معمول: آب، آب آتش‌نشانی و آب شیرین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N101: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O101: INFERRED – PC-ME 14040105 Pazanan2 PUMPS B11: no "NACE MR-0175" line in item description, while the document states it item-by-item where required → N
Note on S101: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y101: SOURCE – PC-ME PUMPS F7: «GOING UNIT PRICE FOB EUR 1404Q1»
Note on AF101: شرط تحویل: FOB (صریح؛ سرستون F7 «GOING UNIT PRICE FOB EUR 1404Q1»). این قیمت = میانگین پیشنهادهای فروشندگان (Vendor_Quotes). این قیمت شامل نیست: ضریب سربار تأمین کالا ×۱٫۱۸ و مالیات بر ارزش افزوده ۱۰٪ (PUMPS G30:H31)، حمل از بندر، بیمه، ترخیص و نصب. شمول یدکی و TPI در پیشنهادها مشخص نیست.
Note on E102: ROT-INJ = Produced Water & Disposal Injection Pumps آب تولیدی و پساب: Booster و پمپ‌های پرفشار تزریق به چاه دفعی
Note on F102: BB3 – Between bearings, multistage, axially split: چندمرحله‌ای، بدنه دوتکه افقی؛ تزریق آب و انتقال پرفشار
Note on G102: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N102: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O102: SOURCE – PC-ME 14040105 Pazanan2 PUMPS B12: NACE 'MR-0175' Required: Yes
Note on S102: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y102: SOURCE – PC-ME PUMPS F7: «GOING UNIT PRICE FOB EUR 1404Q1»
Note on AF102: شرط تحویل: FOB (صریح؛ سرستون F7 «GOING UNIT PRICE FOB EUR 1404Q1»). این قیمت = میانگین پیشنهادهای فروشندگان (Vendor_Quotes). این قیمت شامل نیست: ضریب سربار تأمین کالا ×۱٫۱۸ و مالیات بر ارزش افزوده ۱۰٪ (PUMPS G30:H31)، حمل از بندر، بیمه، ترخیص و نصب. شمول یدکی و TPI در پیشنهادها مشخص نیست.
Note on E103: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن — Reclassified 1405-07: ROT-CRU → ROT-DRN (service-based classification; approved)
Note on F103: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G103: D-1: بدنه داپلکس، پروانه داپلکس؛ رینگ با روکش سخت؛ شفت داپلکس. کاربرد معمول: آب شور و آب تولیدی دارای کلراید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N103: SOURCE – design code line "& IPS-M-PM-140" in the project item description
Note on O103: SOURCE – PC-ME 14040105 Pazanan2 PUMPS B13: NACE 'MR-0175' Required: Yes
Note on S103: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y103: SOURCE – PC-ME PUMPS F7: «GOING UNIT PRICE FOB EUR 1404Q1»
Note on AF103: شرط تحویل: FOB (صریح؛ سرستون F7 «GOING UNIT PRICE FOB EUR 1404Q1»). این قیمت = میانگین پیشنهادهای فروشندگان (Vendor_Quotes). این قیمت شامل نیست: ضریب سربار تأمین کالا ×۱٫۱۸ و مالیات بر ارزش افزوده ۱۰٪ (PUMPS G30:H31)، حمل از بندر، بیمه، ترخیص و نصب. شمول یدکی و TPI در پیشنهادها مشخص نیست.
Note on E104: ROT-INJ = Produced Water & Disposal Injection Pumps آب تولیدی و پساب: Booster و پمپ‌های پرفشار تزریق به چاه دفعی
Note on F104: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G104: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N104: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O104: INFERRED – PC-ME 14040105 Pazanan2 PUMPS B14: no "NACE MR-0175" line in item description, while the document states it item-by-item where required → N
Note on S104: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y104: SOURCE – PC-ME PUMPS F7: «GOING UNIT PRICE FOB EUR 1404Q1»
Note on AF104: شرط تحویل: FOB (صریح؛ سرستون F7 «GOING UNIT PRICE FOB EUR 1404Q1»). این قیمت = میانگین پیشنهادهای فروشندگان (Vendor_Quotes). این قیمت شامل نیست: ضریب سربار تأمین کالا ×۱٫۱۸ و مالیات بر ارزش افزوده ۱۰٪ (PUMPS G30:H31)، حمل از بندر، بیمه، ترخیص و نصب. شمول یدکی و TPI در پیشنهادها مشخص نیست.
Note on E105: ROT-INJ = Produced Water & Disposal Injection Pumps آب تولیدی و پساب: Booster و پمپ‌های پرفشار تزریق به چاه دفعی
Note on F105: BB3 – Between bearings, multistage, axially split: چندمرحله‌ای، بدنه دوتکه افقی؛ تزریق آب و انتقال پرفشار
Note on G105: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N105: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O105: SOURCE – PC-ME 14040105 Pazanan2 PUMPS B15: NACE 'MR-0175' Required: Yes
Note on S105: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y105: SOURCE – PC-ME PUMPS F7: «GOING UNIT PRICE FOB EUR 1404Q1»
Note on AF105: شرط تحویل: FOB (صریح؛ سرستون F7 «GOING UNIT PRICE FOB EUR 1404Q1»). این قیمت = میانگین پیشنهادهای فروشندگان (Vendor_Quotes). این قیمت شامل نیست: ضریب سربار تأمین کالا ×۱٫۱۸ و مالیات بر ارزش افزوده ۱۰٪ (PUMPS G30:H31)، حمل از بندر، بیمه، ترخیص و نصب. شمول یدکی و TPI در پیشنهادها مشخص نیست.
Note on E106: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن
Note on F106: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G106: S-6: بدنه فولاد کربنی، پروانه کروم ۱۲٪؛ رینگ کروم ۱۲٪ سخت‌شده؛ شفت کروم ۱۲٪. کاربرد معمول: هیدروکربن داغ، آب ترش و خوردگی ملایم. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N106: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O106: INFERRED – PC-ME 14040105 Pazanan2 PUMPS B16: no "NACE MR-0175" line in item description, while the document states it item-by-item where required → N
Note on S106: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y106: SOURCE – PC-ME PUMPS F7: «GOING UNIT PRICE FOB EUR 1404Q1»
Note on AF106: شرط تحویل: FOB (صریح؛ سرستون F7 «GOING UNIT PRICE FOB EUR 1404Q1»). این قیمت = میانگین پیشنهادهای فروشندگان (Vendor_Quotes). این قیمت شامل نیست: ضریب سربار تأمین کالا ×۱٫۱۸ و مالیات بر ارزش افزوده ۱۰٪ (PUMPS G30:H31)، حمل از بندر، بیمه، ترخیص و نصب. شمول یدکی و TPI در پیشنهادها مشخص نیست.
Note on E107: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن
Note on F107: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G107: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N107: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O107: SOURCE – PC-ME 14040105 Pazanan2 PUMPS B17: NACE 'MR-0175' Required: Yes
Note on S107: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y107: SOURCE – PC-ME PUMPS F7: «GOING UNIT PRICE FOB EUR 1404Q1»
Note on AF107: شرط تحویل: FOB (صریح؛ سرستون F7 «GOING UNIT PRICE FOB EUR 1404Q1»). این قیمت = میانگین پیشنهادهای فروشندگان (Vendor_Quotes). این قیمت شامل نیست: ضریب سربار تأمین کالا ×۱٫۱۸ و مالیات بر ارزش افزوده ۱۰٪ (PUMPS G30:H31)، حمل از بندر، بیمه، ترخیص و نصب. شمول یدکی و TPI در پیشنهادها مشخص نیست.
Note on E108: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن
Note on F108: VS4 – Vertically suspended, line-shaft, separate discharge (sump): پمپ عمودی Sump با شفت بلند و لوله خروجی جدا؛ چاهک درین و Flare KO
Note on G108: S-6: بدنه فولاد کربنی، پروانه کروم ۱۲٪؛ رینگ کروم ۱۲٪ سخت‌شده؛ شفت کروم ۱۲٪. کاربرد معمول: هیدروکربن داغ، آب ترش و خوردگی ملایم. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N108: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O108: INFERRED – PC-ME 14040105 Pazanan2 PUMPS B18: no "NACE MR-0175" line in item description, while the document states it item-by-item where required → N
Note on S108: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y108: SOURCE – PC-ME PUMPS F7: «GOING UNIT PRICE FOB EUR 1404Q1»
Note on AF108: شرط تحویل: FOB (صریح؛ سرستون F7 «GOING UNIT PRICE FOB EUR 1404Q1»). این قیمت = میانگین پیشنهادهای فروشندگان (Vendor_Quotes). این قیمت شامل نیست: ضریب سربار تأمین کالا ×۱٫۱۸ و مالیات بر ارزش افزوده ۱۰٪ (PUMPS G30:H31)، حمل از بندر، بیمه، ترخیص و نصب. شمول یدکی و TPI در پیشنهادها مشخص نیست.
Note on E109: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن — Reclassified 1405-07: ROT-CRU → ROT-DRN (service-based classification; approved)
Note on F109: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G109: D-1: بدنه داپلکس، پروانه داپلکس؛ رینگ با روکش سخت؛ شفت داپلکس. کاربرد معمول: آب شور و آب تولیدی دارای کلراید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N109: SOURCE – design code line "& IPS-M-PM-140" in the project item description
Note on O109: SOURCE – PC-ME 14040105 Pazanan2 PUMPS B19: NACE 'MR-0175' Required: Yes
Note on S109: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y109: SOURCE – PC-ME Cover D65: نسخه R02 = FEB 2015 (بهمن ۱۳۹۳)
Note on AA109: SOURCE – PC-ME 14040105 Pazanan2 PUMPS F19: =AR19*'[5]Basic INFO'!$C$138 – no quotation received (all declined); AR19 = R02 (1393) FOB price 25,000 EUR × 1.552
Note on AF109: شرط تحویل: FOB (صریح؛ سرستون AR7 «Unit Price 'FOB' (€)»، نسخه R02 فوریه ۲۰۱۵ = بهمن ۱۳۹۳). این قیمت = قیمت واحد برآوردی R02 بدون سربار؛ حمل، بیمه، ترخیص، سربار، مالیات و نصب شامل نیست.
Note on E110: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F110: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G110: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N110: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O110: SOURCE – PC-ME 14040105 Pazanan2 PUMPS B20: NACE 'MR-0175' Required: Yes
Note on S110: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y110: SOURCE – PC-ME PUMPS F7: «GOING UNIT PRICE FOB EUR 1404Q1»
Note on AF110: شرط تحویل: FOB (صریح؛ سرستون F7 «GOING UNIT PRICE FOB EUR 1404Q1»). این قیمت = میانگین پیشنهادهای فروشندگان (Vendor_Quotes). این قیمت شامل نیست: ضریب سربار تأمین کالا ×۱٫۱۸ و مالیات بر ارزش افزوده ۱۰٪ (PUMPS G30:H31)، حمل از بندر، بیمه، ترخیص و نصب. شمول یدکی و TPI در پیشنهادها مشخص نیست.
Note on E111: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن
Note on F111: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G111: S-6: بدنه فولاد کربنی، پروانه کروم ۱۲٪؛ رینگ کروم ۱۲٪ سخت‌شده؛ شفت کروم ۱۲٪. کاربرد معمول: هیدروکربن داغ، آب ترش و خوردگی ملایم. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N111: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O111: INFERRED – PC-ME 14040105 Pazanan2 PUMPS B21: no "NACE MR-0175" line in item description, while the document states it item-by-item where required → N
Note on S111: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y111: SOURCE – PC-ME PUMPS F7: «GOING UNIT PRICE FOB EUR 1404Q1»
Note on AF111: شرط تحویل: FOB (صریح؛ سرستون F7 «GOING UNIT PRICE FOB EUR 1404Q1»). این قیمت = میانگین پیشنهادهای فروشندگان (Vendor_Quotes). این قیمت شامل نیست: ضریب سربار تأمین کالا ×۱٫۱۸ و مالیات بر ارزش افزوده ۱۰٪ (PUMPS G30:H31)، حمل از بندر، بیمه، ترخیص و نصب. شمول یدکی و TPI در پیشنهادها مشخص نیست.
Note on E112: ROT-AUX = Chemical, Fuel & Auxiliary Pumps پمپ‌های جانبی: مواد شیمیایی، گلایکول، گازوئیل و سوخت
Note on F112: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G112: S-1: بدنه فولاد کربنی، پروانه چدن؛ رینگ چدن؛ شفت فولاد کربنی. کاربرد معمول: هیدروکربن غیرخورنده. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N112: SOURCE – design code line "& IPS-M-PM-115" in the project item description
Note on O112: INFERRED – PC-ME 14040105 Pazanan2 PUMPS B22: no "NACE MR-0175" line in item description, while the document states it item-by-item where required → N
Note on S112: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y112: SOURCE – PC-ME PUMPS F7: «GOING UNIT PRICE FOB EUR 1404Q1»
Note on AF112: شرط تحویل: FOB (صریح؛ سرستون F7 «GOING UNIT PRICE FOB EUR 1404Q1»). این قیمت = میانگین پیشنهادهای فروشندگان (Vendor_Quotes). این قیمت شامل نیست: ضریب سربار تأمین کالا ×۱٫۱۸ و مالیات بر ارزش افزوده ۱۰٪ (PUMPS G30:H31)، حمل از بندر، بیمه، ترخیص و نصب. شمول یدکی و TPI در پیشنهادها مشخص نیست.
Note on E113: ROT-FIR = Firewater & Safety Pumps آتش‌نشانی: پمپ اصلی برقی و دیزلی، Jockey و بارگیری آب آتش‌نشانی
Note on F113: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G113: I-2: بدنه چدن، پروانه برنز؛ رینگ برنز؛ شفت فولاد کربنی. کاربرد معمول: آب، آب آتش‌نشانی و آب شیرین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N113: SOURCE – design code line "& IPS-M-PM-115" in the project item description
Note on O113: INFERRED – PC-ME 14040105 Pazanan2 PUMPS B23: no "NACE MR-0175" line in item description, while the document states it item-by-item where required → N
Note on S113: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y113: SOURCE – PC-ME PUMPS F7: «GOING UNIT PRICE FOB EUR 1404Q1»
Note on AF113: شرط تحویل: FOB (صریح؛ سرستون F7 «GOING UNIT PRICE FOB EUR 1404Q1»). این قیمت = میانگین پیشنهادهای فروشندگان (Vendor_Quotes). این قیمت شامل نیست: ضریب سربار تأمین کالا ×۱٫۱۸ و مالیات بر ارزش افزوده ۱۰٪ (PUMPS G30:H31)، حمل از بندر، بیمه، ترخیص و نصب. شمول یدکی و TPI در پیشنهادها مشخص نیست.
Note on E114: ROT-FIR = Firewater & Safety Pumps آتش‌نشانی: پمپ اصلی برقی و دیزلی، Jockey و بارگیری آب آتش‌نشانی
Note on F114: BB (unspecified) – Between bearings – subtype not stated: منبع فقط «Between Bearings» گفته و زیرنوع API را مشخص نکرده
Note on G114: I-2: بدنه چدن، پروانه برنز؛ رینگ برنز؛ شفت فولاد کربنی. کاربرد معمول: آب، آب آتش‌نشانی و آب شیرین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N114: SOURCE – design code line "& IPS-M-PM-125" in the project item description
Note on O114: INFERRED – PC-ME 14040105 Pazanan2 PUMPS B24: no "NACE MR-0175" line in item description, while the document states it item-by-item where required → N
Note on S114: SOURCE – equipment name states electric motor driven
Note on Y114: SOURCE – PC-ME PUMPS F7: «GOING UNIT PRICE FOB EUR 1404Q1»
Note on AF114: شرط تحویل: FOB (صریح؛ سرستون F7 «GOING UNIT PRICE FOB EUR 1404Q1»). این قیمت = میانگین پیشنهادهای فروشندگان (Vendor_Quotes). این قیمت شامل نیست: ضریب سربار تأمین کالا ×۱٫۱۸ و مالیات بر ارزش افزوده ۱۰٪ (PUMPS G30:H31)، حمل از بندر، بیمه، ترخیص و نصب. شمول یدکی و TPI در پیشنهادها مشخص نیست.
Note on E115: ROT-FIR = Firewater & Safety Pumps آتش‌نشانی: پمپ اصلی برقی و دیزلی، Jockey و بارگیری آب آتش‌نشانی
Note on F115: BB (unspecified) – Between bearings – subtype not stated: منبع فقط «Between Bearings» گفته و زیرنوع API را مشخص نکرده
Note on G115: I-2: بدنه چدن، پروانه برنز؛ رینگ برنز؛ شفت فولاد کربنی. کاربرد معمول: آب، آب آتش‌نشانی و آب شیرین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N115: SOURCE – design code line "& IPS-M-PM-125" in the project item description
Note on O115: INFERRED – PC-ME 14040105 Pazanan2 PUMPS B25: no "NACE MR-0175" line in item description, while the document states it item-by-item where required → N
Note on S115: SOURCE – equipment name states diesel engine driven
Note on Y115: SOURCE – PC-ME PUMPS F7: «GOING UNIT PRICE FOB EUR 1404Q1»
Note on AF115: شرط تحویل: FOB (صریح؛ سرستون F7 «GOING UNIT PRICE FOB EUR 1404Q1»). این قیمت = میانگین پیشنهادهای فروشندگان (Vendor_Quotes). این قیمت شامل نیست: ضریب سربار تأمین کالا ×۱٫۱۸ و مالیات بر ارزش افزوده ۱۰٪ (PUMPS G30:H31)، حمل از بندر، بیمه، ترخیص و نصب. شمول یدکی و TPI در پیشنهادها مشخص نیست.
Note on E116: ROT-FIR = Firewater & Safety Pumps آتش‌نشانی: پمپ اصلی برقی و دیزلی، Jockey و بارگیری آب آتش‌نشانی
Note on F116: OH (unspecified) – Overhung – subtype not stated: منبع فقط «Overhung» گفته و زیرنوع API را مشخص نکرده
Note on G116: I-2: بدنه چدن، پروانه برنز؛ رینگ برنز؛ شفت فولاد کربنی. کاربرد معمول: آب، آب آتش‌نشانی و آب شیرین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N116: SOURCE – design code line "& IPS-M-PM-125" in the project item description
Note on O116: INFERRED – PC-ME 14040105 Pazanan2 PUMPS B26: no "NACE MR-0175" line in item description, while the document states it item-by-item where required → N
Note on S116: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y116: SOURCE – PC-ME PUMPS F7: «GOING UNIT PRICE FOB EUR 1404Q1»
Note on AF116: شرط تحویل: FOB (صریح؛ سرستون F7 «GOING UNIT PRICE FOB EUR 1404Q1»). این قیمت = میانگین پیشنهادهای فروشندگان (Vendor_Quotes). این قیمت شامل نیست: ضریب سربار تأمین کالا ×۱٫۱۸ و مالیات بر ارزش افزوده ۱۰٪ (PUMPS G30:H31)، حمل از بندر، بیمه، ترخیص و نصب. شمول یدکی و TPI در پیشنهادها مشخص نیست.
Note on E117: ROT-AUX = Chemical, Fuel & Auxiliary Pumps پمپ‌های جانبی: مواد شیمیایی، گلایکول، گازوئیل و سوخت — Reclassified 1405-07: ROT-INJ → ROT-AUX (service-based classification; approved)
Note on F117: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G117: SS316L (non-API): بدنه فولاد ضدزنگ 316L، پروانه فولاد ضدزنگ 316L؛ —. کاربرد معمول: ساخت غیر API (مثلاً پمپ بشکه‌ای پرتابل). (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on H117: SOURCE – PC-ME 14040105 Pazanan2 PUMPS B27: Rated Flow 160 Lit/min = 9.6 m3/hr (previous bank had 160 m3/h – unit error)
Note on M117: Source item gives type / flow / material only – no design standard (previous bank "API 610 / IPS" unsupported; a portable barrel pump is not an API 610 pump)
Note on O117: INFERRED – PC-ME 14040105 Pazanan2 PUMPS B27: no "NACE MR-0175" line in item description, while the document states it item-by-item where required → N
Note on S117: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y117: SOURCE – PC-ME Cover D65: نسخه R02 = FEB 2015 (بهمن ۱۳۹۳)
Note on AA117: SOURCE – PC-ME 14040105 Pazanan2 PUMPS E27: =AQ27*'[5]Basic INFO'!$E$127 – no quotation received (all declined); value is the R02 (1393) price AQ27 = 100,000,000 IRR escalated by an external factor
Note on AF117: شرط تحویل: در منبع ذکر نشده (قیمت ریالی R02، ستون AQ «Unit Price (Rials)»). سربار، مالیات و نصب شامل نیست.
Note on E118: ROT-AUX = Chemical, Fuel & Auxiliary Pumps پمپ‌های جانبی: مواد شیمیایی، گلایکول، گازوئیل و سوخت — Reclassified 1405-07: ROT-INJ → ROT-AUX (service-based classification; approved)
Note on F118: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G118: SS316L (non-API): بدنه فولاد ضدزنگ 316L، پروانه فولاد ضدزنگ 316L؛ —. کاربرد معمول: ساخت غیر API (مثلاً پمپ بشکه‌ای پرتابل). (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on H118: SOURCE – PC-ME 14040105 Pazanan2 PUMPS B28: Rated Flow 160 Lit/min = 9.6 m3/hr (previous bank had 160 m3/h – unit error)
Note on M118: Source item gives type / flow / material only – no design standard (previous bank "API 610 / IPS" unsupported; a portable barrel pump is not an API 610 pump)
Note on O118: INFERRED – PC-ME 14040105 Pazanan2 PUMPS B28: no "NACE MR-0175" line in item description, while the document states it item-by-item where required → N
Note on S118: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y118: SOURCE – PC-ME Cover D65: نسخه R02 = FEB 2015 (بهمن ۱۳۹۳)
Note on AA118: SOURCE – PC-ME 14040105 Pazanan2 PUMPS E28: =AQ28*'[5]Basic INFO'!$E$127 – no quotation received (all declined); value is the R02 (1393) price AQ28 = 100,000,000 IRR escalated by an external factor
Note on AF118: شرط تحویل: در منبع ذکر نشده (قیمت ریالی R02، ستون AQ «Unit Price (Rials)»). سربار، مالیات و نصب شامل نیست.
Note on E119: ROT-CRU = Crude Oil & Main Transfer Pumps پمپ‌های نفت خام: انتقال نفت شور و نمک‌زدایی‌شده، Booster، Off-spec و انتقال اصلی
Note on F119: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G119: کلاس متریال در منبع ذکر نشده است.
Note on I119: SOURCE – نمونه قیمتی، شیت PUMPS سلول F4
Note on S119: SOURCE – نمونه قیمتی، شیت PUMPS سلول E4 = E
Note on AF119: شرط تحویل و شمول هزینه‌ها در منبع (نمونه قیمتی، شیت PUMPS ستون H «Price ($)») ذکر نشده است.
Note on E120: ROT-CRU = Crude Oil & Main Transfer Pumps پمپ‌های نفت خام: انتقال نفت شور و نمک‌زدایی‌شده، Booster، Off-spec و انتقال اصلی
Note on F120: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G120: کلاس متریال در منبع ذکر نشده است.
Note on I120: SOURCE – نمونه قیمتی، شیت PUMPS سلول F5
Note on S120: SOURCE – نمونه قیمتی، شیت PUMPS سلول E5 = E
Note on AF120: شرط تحویل و شمول هزینه‌ها در منبع (نمونه قیمتی، شیت PUMPS ستون H «Price ($)») ذکر نشده است.
Note on E121: ROT-CRU = Crude Oil & Main Transfer Pumps پمپ‌های نفت خام: انتقال نفت شور و نمک‌زدایی‌شده، Booster، Off-spec و انتقال اصلی
Note on F121: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G121: کلاس متریال در منبع ذکر نشده است.
Note on I121: SOURCE – نمونه قیمتی، شیت PUMPS سلول F6
Note on S121: SOURCE – نمونه قیمتی، شیت PUMPS سلول E6 = E
Note on AF121: شرط تحویل و شمول هزینه‌ها در منبع (نمونه قیمتی، شیت PUMPS ستون H «Price ($)») ذکر نشده است.
Note on E122: ROT-CRU = Crude Oil & Main Transfer Pumps پمپ‌های نفت خام: انتقال نفت شور و نمک‌زدایی‌شده، Booster، Off-spec و انتقال اصلی
Note on F122: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G122: کلاس متریال در منبع ذکر نشده است.
Note on S122: SOURCE – نمونه قیمتی، شیت PUMPS سلول E7 = E
Note on AF122: شرط تحویل و شمول هزینه‌ها در منبع (نمونه قیمتی، شیت PUMPS ستون H «Price ($)») ذکر نشده است.
Note on E123: ROT-CRU = Crude Oil & Main Transfer Pumps پمپ‌های نفت خام: انتقال نفت شور و نمک‌زدایی‌شده، Booster، Off-spec و انتقال اصلی
Note on F123: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G123: کلاس متریال در منبع ذکر نشده است.
Note on I123: SOURCE – نمونه قیمتی، شیت PUMPS سلول F8
Note on S123: SOURCE – نمونه قیمتی، شیت PUMPS سلول E8 = E
Note on AF123: شرط تحویل و شمول هزینه‌ها در منبع (نمونه قیمتی، شیت PUMPS ستون H «Price ($)») ذکر نشده است.
Note on E124: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F124: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G124: کلاس متریال در منبع ذکر نشده است.
Note on I124: SOURCE – نمونه قیمتی، شیت PUMPS سلول F9
Note on S124: SOURCE – نمونه قیمتی، شیت PUMPS سلول E9 = E
Note on AF124: شرط تحویل و شمول هزینه‌ها در منبع (نمونه قیمتی، شیت PUMPS ستون H «Price ($)») ذکر نشده است.
Note on E125: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F125: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G125: کلاس متریال در منبع ذکر نشده است.
Note on I125: SOURCE – نمونه قیمتی، شیت PUMPS سلول F10
Note on S125: SOURCE – نمونه قیمتی، شیت PUMPS سلول E10 = E
Note on AF125: شرط تحویل و شمول هزینه‌ها در منبع (نمونه قیمتی، شیت PUMPS ستون H «Price ($)») ذکر نشده است.
Note on E126: ROT-INJ = Produced Water & Disposal Injection Pumps آب تولیدی و پساب: Booster و پمپ‌های پرفشار تزریق به چاه دفعی
Note on F126: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G126: کلاس متریال در منبع ذکر نشده است.
Note on I126: SOURCE – نمونه قیمتی، شیت PUMPS سلول F11
Note on S126: SOURCE – نمونه قیمتی، شیت PUMPS سلول E11 = E
Note on AF126: شرط تحویل و شمول هزینه‌ها در منبع (نمونه قیمتی، شیت PUMPS ستون H «Price ($)») ذکر نشده است.
Note on E127: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن — Reclassified 1405-07: ROT-DRN → ROT-WAT (service-based classification; approved)
Note on F127: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G127: کلاس متریال در منبع ذکر نشده است.
Note on I127: SOURCE – نمونه قیمتی، شیت PUMPS سلول F12
Note on S127: SOURCE – نمونه قیمتی، شیت PUMPS سلول E12 = E
Note on AF127: شرط تحویل و شمول هزینه‌ها در منبع (نمونه قیمتی، شیت PUMPS ستون H «Price ($)») ذکر نشده است.
Note on E128: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن
Note on F128: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G128: کلاس متریال در منبع ذکر نشده است.
Note on I128: SOURCE – نمونه قیمتی، شیت PUMPS سلول F13
Note on S128: SOURCE – نمونه قیمتی، شیت PUMPS سلول E13 = E
Note on V128: INFERRED – source does not state pump type; "Centrifugal (assumed)" carried from previous bank
Note on AF128: شرط تحویل و شمول هزینه‌ها در منبع (نمونه قیمتی، شیت PUMPS ستون H «Price ($)») ذکر نشده است.
Note on E129: ROT-AUX = Chemical, Fuel & Auxiliary Pumps پمپ‌های جانبی: مواد شیمیایی، گلایکول، گازوئیل و سوخت
Note on F129: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G129: کلاس متریال در منبع ذکر نشده است.
Note on I129: SOURCE – نمونه قیمتی، شیت PUMPS سلول F14
Note on AF129: شرط تحویل و شمول هزینه‌ها در منبع (نمونه قیمتی، شیت PUMPS ستون H «Price ($)») ذکر نشده است.
Note on E130: ROT-AUX = Chemical, Fuel & Auxiliary Pumps پمپ‌های جانبی: مواد شیمیایی، گلایکول، گازوئیل و سوخت
Note on F130: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G130: کلاس متریال در منبع ذکر نشده است.
Note on I130: SOURCE – نمونه قیمتی، شیت PUMPS سلول F15
Note on J130: SOURCE – نمونه قیمتی، شیت PUMPS سلول G15 = 0.83
Note on S130: SOURCE – نمونه قیمتی، شیت PUMPS سلول E15 = E
Note on AF130: شرط تحویل و شمول هزینه‌ها در منبع (نمونه قیمتی، شیت PUMPS ستون H «Price ($)») ذکر نشده است.
Note on E131: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F131: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G131: کلاس متریال در منبع ذکر نشده است.
Note on S131: SOURCE – نمونه قیمتی، شیت PUMPS سلول E16 = E
Note on AF131: شرط تحویل و شمول هزینه‌ها در منبع (نمونه قیمتی، شیت PUMPS ستون H «Price ($)») ذکر نشده است.
Note on E132: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن
Note on F132: Not stated – —: نوع پمپ در منبع ذکر نشده
Note on G132: کلاس متریال در منبع ذکر نشده است.
Note on S132: SOURCE – نمونه قیمتی، شیت PUMPS سلول E17 = E
Note on AF132: شرط تحویل و شمول هزینه‌ها در منبع (نمونه قیمتی، شیت PUMPS ستون H «Price ($)») ذکر نشده است.
Note on E133: ROT-CRU = Crude Oil & Main Transfer Pumps پمپ‌های نفت خام: انتقال نفت شور و نمک‌زدایی‌شده، Booster، Off-spec و انتقال اصلی
Note on F133: VS6 – Vertically suspended, double casing, diffuser (can): عمودی دوبدنه در قوطی (Can)؛ NPSH کم، مثل Off-spec و مایعات نزدیک نقطه جوش
Note on G133: D-1: بدنه داپلکس، پروانه داپلکس؛ رینگ با روکش سخت؛ شفت داپلکس. کاربرد معمول: آب شور و آب تولیدی دارای کلراید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N133: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O133: SOURCE – PC-ME 14040105 Pazanan2 PUMPS B8: NACE 'MR-0175' Required: Yes
Note on S133: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y133: SOURCE – PC-ME Cover D65: نسخه R02 = FEB 2015 (بهمن ۱۳۹۳)
Note on Z133: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR8
Note on AA133: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR8: R02 (1393) FOB unit price
Note on AF133: شرط تحویل: FOB (صریح؛ سرستون AR7 «Unit Price 'FOB' (€)»، نسخه R02 فوریه ۲۰۱۵ = بهمن ۱۳۹۳). این قیمت = قیمت واحد برآوردی R02 بدون سربار؛ حمل، بیمه، ترخیص، سربار، مالیات و نصب شامل نیست.
Note on E134: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F134: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G134: I-2: بدنه چدن، پروانه برنز؛ رینگ برنز؛ شفت فولاد کربنی. کاربرد معمول: آب، آب آتش‌نشانی و آب شیرین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N134: SOURCE – design code line "& IPS-M-PM-115" in the project item description
Note on O134: INFERRED – PC-ME 14040105 Pazanan2 PUMPS B9: no "NACE MR-0175" line in item description, while the document states it item-by-item where required → N
Note on S134: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y134: SOURCE – PC-ME Cover D65: نسخه R02 = FEB 2015 (بهمن ۱۳۹۳)
Note on Z134: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR9
Note on AA134: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR9: R02 (1393) FOB unit price
Note on AF134: شرط تحویل: FOB (صریح؛ سرستون AR7 «Unit Price 'FOB' (€)»، نسخه R02 فوریه ۲۰۱۵ = بهمن ۱۳۹۳). این قیمت = قیمت واحد برآوردی R02 بدون سربار؛ حمل، بیمه، ترخیص، سربار، مالیات و نصب شامل نیست.
Note on E135: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F135: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G135: I-2: بدنه چدن، پروانه برنز؛ رینگ برنز؛ شفت فولاد کربنی. کاربرد معمول: آب، آب آتش‌نشانی و آب شیرین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N135: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O135: INFERRED – PC-ME 14040105 Pazanan2 PUMPS B10: no "NACE MR-0175" line in item description, while the document states it item-by-item where required → N
Note on S135: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y135: SOURCE – PC-ME Cover D65: نسخه R02 = FEB 2015 (بهمن ۱۳۹۳)
Note on Z135: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR10
Note on AA135: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR10: R02 (1393) FOB unit price
Note on AF135: شرط تحویل: FOB (صریح؛ سرستون AR7 «Unit Price 'FOB' (€)»، نسخه R02 فوریه ۲۰۱۵ = بهمن ۱۳۹۳). این قیمت = قیمت واحد برآوردی R02 بدون سربار؛ حمل، بیمه، ترخیص، سربار، مالیات و نصب شامل نیست.
Note on E136: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F136: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G136: I-2: بدنه چدن، پروانه برنز؛ رینگ برنز؛ شفت فولاد کربنی. کاربرد معمول: آب، آب آتش‌نشانی و آب شیرین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N136: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O136: INFERRED – PC-ME 14040105 Pazanan2 PUMPS B11: no "NACE MR-0175" line in item description, while the document states it item-by-item where required → N
Note on S136: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y136: SOURCE – PC-ME Cover D65: نسخه R02 = FEB 2015 (بهمن ۱۳۹۳)
Note on Z136: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR11
Note on AA136: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR11: R02 (1393) FOB unit price
Note on AF136: شرط تحویل: FOB (صریح؛ سرستون AR7 «Unit Price 'FOB' (€)»، نسخه R02 فوریه ۲۰۱۵ = بهمن ۱۳۹۳). این قیمت = قیمت واحد برآوردی R02 بدون سربار؛ حمل، بیمه، ترخیص، سربار، مالیات و نصب شامل نیست.
Note on E137: ROT-INJ = Produced Water & Disposal Injection Pumps آب تولیدی و پساب: Booster و پمپ‌های پرفشار تزریق به چاه دفعی
Note on F137: BB3 – Between bearings, multistage, axially split: چندمرحله‌ای، بدنه دوتکه افقی؛ تزریق آب و انتقال پرفشار
Note on G137: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N137: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O137: SOURCE – PC-ME 14040105 Pazanan2 PUMPS B12: NACE 'MR-0175' Required: Yes
Note on S137: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y137: SOURCE – PC-ME Cover D65: نسخه R02 = FEB 2015 (بهمن ۱۳۹۳)
Note on Z137: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR12
Note on AA137: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR12: R02 (1393) FOB unit price
Note on AF137: شرط تحویل: FOB (صریح؛ سرستون AR7 «Unit Price 'FOB' (€)»، نسخه R02 فوریه ۲۰۱۵ = بهمن ۱۳۹۳). این قیمت = قیمت واحد برآوردی R02 بدون سربار؛ حمل، بیمه، ترخیص، سربار، مالیات و نصب شامل نیست.
Note on E138: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن — Reclassified 1405-07: ROT-CRU → ROT-DRN (service-based classification; approved)
Note on F138: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G138: D-1: بدنه داپلکس، پروانه داپلکس؛ رینگ با روکش سخت؛ شفت داپلکس. کاربرد معمول: آب شور و آب تولیدی دارای کلراید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N138: SOURCE – design code line "& IPS-M-PM-140" in the project item description
Note on O138: SOURCE – PC-ME 14040105 Pazanan2 PUMPS B13: NACE 'MR-0175' Required: Yes
Note on S138: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y138: SOURCE – PC-ME Cover D65: نسخه R02 = FEB 2015 (بهمن ۱۳۹۳)
Note on Z138: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR13
Note on AA138: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR13: R02 (1393) FOB unit price
Note on AF138: شرط تحویل: FOB (صریح؛ سرستون AR7 «Unit Price 'FOB' (€)»، نسخه R02 فوریه ۲۰۱۵ = بهمن ۱۳۹۳). این قیمت = قیمت واحد برآوردی R02 بدون سربار؛ حمل، بیمه، ترخیص، سربار، مالیات و نصب شامل نیست.
Note on E139: ROT-INJ = Produced Water & Disposal Injection Pumps آب تولیدی و پساب: Booster و پمپ‌های پرفشار تزریق به چاه دفعی
Note on F139: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G139: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N139: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O139: INFERRED – PC-ME 14040105 Pazanan2 PUMPS B14: no "NACE MR-0175" line in item description, while the document states it item-by-item where required → N
Note on S139: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y139: SOURCE – PC-ME Cover D65: نسخه R02 = FEB 2015 (بهمن ۱۳۹۳)
Note on Z139: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR14
Note on AA139: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR14: R02 (1393) FOB unit price
Note on AF139: شرط تحویل: FOB (صریح؛ سرستون AR7 «Unit Price 'FOB' (€)»، نسخه R02 فوریه ۲۰۱۵ = بهمن ۱۳۹۳). این قیمت = قیمت واحد برآوردی R02 بدون سربار؛ حمل، بیمه، ترخیص، سربار، مالیات و نصب شامل نیست.
Note on E140: ROT-INJ = Produced Water & Disposal Injection Pumps آب تولیدی و پساب: Booster و پمپ‌های پرفشار تزریق به چاه دفعی
Note on F140: BB3 – Between bearings, multistage, axially split: چندمرحله‌ای، بدنه دوتکه افقی؛ تزریق آب و انتقال پرفشار
Note on G140: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N140: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O140: SOURCE – PC-ME 14040105 Pazanan2 PUMPS B15: NACE 'MR-0175' Required: Yes
Note on S140: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y140: SOURCE – PC-ME Cover D65: نسخه R02 = FEB 2015 (بهمن ۱۳۹۳)
Note on Z140: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR15
Note on AA140: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR15: R02 (1393) FOB unit price
Note on AF140: شرط تحویل: FOB (صریح؛ سرستون AR7 «Unit Price 'FOB' (€)»، نسخه R02 فوریه ۲۰۱۵ = بهمن ۱۳۹۳). این قیمت = قیمت واحد برآوردی R02 بدون سربار؛ حمل، بیمه، ترخیص، سربار، مالیات و نصب شامل نیست.
Note on E141: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن
Note on F141: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G141: S-6: بدنه فولاد کربنی، پروانه کروم ۱۲٪؛ رینگ کروم ۱۲٪ سخت‌شده؛ شفت کروم ۱۲٪. کاربرد معمول: هیدروکربن داغ، آب ترش و خوردگی ملایم. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N141: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O141: INFERRED – PC-ME 14040105 Pazanan2 PUMPS B16: no "NACE MR-0175" line in item description, while the document states it item-by-item where required → N
Note on S141: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y141: SOURCE – PC-ME Cover D65: نسخه R02 = FEB 2015 (بهمن ۱۳۹۳)
Note on Z141: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR16
Note on AA141: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR16: R02 (1393) FOB unit price
Note on AF141: شرط تحویل: FOB (صریح؛ سرستون AR7 «Unit Price 'FOB' (€)»، نسخه R02 فوریه ۲۰۱۵ = بهمن ۱۳۹۳). این قیمت = قیمت واحد برآوردی R02 بدون سربار؛ حمل، بیمه، ترخیص، سربار، مالیات و نصب شامل نیست.
Note on E142: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن
Note on F142: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G142: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N142: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O142: SOURCE – PC-ME 14040105 Pazanan2 PUMPS B17: NACE 'MR-0175' Required: Yes
Note on S142: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y142: SOURCE – PC-ME Cover D65: نسخه R02 = FEB 2015 (بهمن ۱۳۹۳)
Note on Z142: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR17
Note on AA142: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR17: R02 (1393) FOB unit price
Note on AF142: شرط تحویل: FOB (صریح؛ سرستون AR7 «Unit Price 'FOB' (€)»، نسخه R02 فوریه ۲۰۱۵ = بهمن ۱۳۹۳). این قیمت = قیمت واحد برآوردی R02 بدون سربار؛ حمل، بیمه، ترخیص، سربار، مالیات و نصب شامل نیست.
Note on E143: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن
Note on F143: VS4 – Vertically suspended, line-shaft, separate discharge (sump): پمپ عمودی Sump با شفت بلند و لوله خروجی جدا؛ چاهک درین و Flare KO
Note on G143: S-6: بدنه فولاد کربنی، پروانه کروم ۱۲٪؛ رینگ کروم ۱۲٪ سخت‌شده؛ شفت کروم ۱۲٪. کاربرد معمول: هیدروکربن داغ، آب ترش و خوردگی ملایم. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N143: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O143: INFERRED – PC-ME 14040105 Pazanan2 PUMPS B18: no "NACE MR-0175" line in item description, while the document states it item-by-item where required → N
Note on S143: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y143: SOURCE – PC-ME Cover D65: نسخه R02 = FEB 2015 (بهمن ۱۳۹۳)
Note on Z143: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR18
Note on AA143: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR18: R02 (1393) FOB unit price
Note on AF143: شرط تحویل: FOB (صریح؛ سرستون AR7 «Unit Price 'FOB' (€)»، نسخه R02 فوریه ۲۰۱۵ = بهمن ۱۳۹۳). این قیمت = قیمت واحد برآوردی R02 بدون سربار؛ حمل، بیمه، ترخیص، سربار، مالیات و نصب شامل نیست.
Note on E144: ROT-WAT = Desalting & Process Water Pumps آب فرآیندی واحد: آب رقیق‌سازی، Recycle دیسالتر، آب هوازدایی‌شده، آب شیرین و آب خنک‌کن
Note on F144: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G144: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N144: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O144: SOURCE – PC-ME 14040105 Pazanan2 PUMPS B20: NACE 'MR-0175' Required: Yes
Note on S144: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y144: SOURCE – PC-ME Cover D65: نسخه R02 = FEB 2015 (بهمن ۱۳۹۳)
Note on Z144: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR20
Note on AA144: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR20: R02 (1393) FOB unit price
Note on AF144: شرط تحویل: FOB (صریح؛ سرستون AR7 «Unit Price 'FOB' (€)»، نسخه R02 فوریه ۲۰۱۵ = بهمن ۱۳۹۳). این قیمت = قیمت واحد برآوردی R02 بدون سربار؛ حمل، بیمه، ترخیص، سربار، مالیات و نصب شامل نیست.
Note on E145: ROT-DRN = Drainage, Flare & OWS Pumps درین بسته و باز، Flare KO Drum، جداکننده آب و نفت (OWS)، نفت بازیافتی و لجن
Note on F145: OH2 – Overhung, centreline-mounted: یک‌مرحله‌ای Overhung با نصب روی خط مرکز؛ رایج‌ترین پمپ فرآیندی پالایشگاهی و تحمل دمای بالا
Note on G145: S-6: بدنه فولاد کربنی، پروانه کروم ۱۲٪؛ رینگ کروم ۱۲٪ سخت‌شده؛ شفت کروم ۱۲٪. کاربرد معمول: هیدروکربن داغ، آب ترش و خوردگی ملایم. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N145: SOURCE – design code line "& IPS-G-PM-105" in the project item description
Note on O145: INFERRED – PC-ME 14040105 Pazanan2 PUMPS B21: no "NACE MR-0175" line in item description, while the document states it item-by-item where required → N
Note on S145: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y145: SOURCE – PC-ME Cover D65: نسخه R02 = FEB 2015 (بهمن ۱۳۹۳)
Note on Z145: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR21
Note on AA145: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR21: R02 (1393) FOB unit price
Note on AF145: شرط تحویل: FOB (صریح؛ سرستون AR7 «Unit Price 'FOB' (€)»، نسخه R02 فوریه ۲۰۱۵ = بهمن ۱۳۹۳). این قیمت = قیمت واحد برآوردی R02 بدون سربار؛ حمل، بیمه، ترخیص، سربار، مالیات و نصب شامل نیست.
Note on E146: ROT-AUX = Chemical, Fuel & Auxiliary Pumps پمپ‌های جانبی: مواد شیمیایی، گلایکول، گازوئیل و سوخت
Note on F146: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G146: S-1: بدنه فولاد کربنی، پروانه چدن؛ رینگ چدن؛ شفت فولاد کربنی. کاربرد معمول: هیدروکربن غیرخورنده. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N146: SOURCE – design code line "& IPS-M-PM-115" in the project item description
Note on O146: INFERRED – PC-ME 14040105 Pazanan2 PUMPS B22: no "NACE MR-0175" line in item description, while the document states it item-by-item where required → N
Note on S146: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y146: SOURCE – PC-ME Cover D65: نسخه R02 = FEB 2015 (بهمن ۱۳۹۳)
Note on Z146: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR22
Note on AA146: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR22: R02 (1393) FOB unit price
Note on AF146: شرط تحویل: FOB (صریح؛ سرستون AR7 «Unit Price 'FOB' (€)»، نسخه R02 فوریه ۲۰۱۵ = بهمن ۱۳۹۳). این قیمت = قیمت واحد برآوردی R02 بدون سربار؛ حمل، بیمه، ترخیص، سربار، مالیات و نصب شامل نیست.
Note on E147: ROT-FIR = Firewater & Safety Pumps آتش‌نشانی: پمپ اصلی برقی و دیزلی، Jockey و بارگیری آب آتش‌نشانی
Note on F147: N/A (non-API 610) – Not an API 610 pump: پمپ طبق API 610 نیست (ISO 5199، NFPA 20، JIS، پمپ جابه‌جایی مثبت یا پرتابل)؛ طبقه‌بندی API 610 کاربرد ندارد
Note on G147: I-2: بدنه چدن، پروانه برنز؛ رینگ برنز؛ شفت فولاد کربنی. کاربرد معمول: آب، آب آتش‌نشانی و آب شیرین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N147: SOURCE – design code line "& IPS-M-PM-115" in the project item description
Note on O147: INFERRED – PC-ME 14040105 Pazanan2 PUMPS B23: no "NACE MR-0175" line in item description, while the document states it item-by-item where required → N
Note on S147: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y147: SOURCE – PC-ME Cover D65: نسخه R02 = FEB 2015 (بهمن ۱۳۹۳)
Note on Z147: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR23
Note on AA147: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR23: R02 (1393) FOB unit price
Note on AF147: شرط تحویل: FOB (صریح؛ سرستون AR7 «Unit Price 'FOB' (€)»، نسخه R02 فوریه ۲۰۱۵ = بهمن ۱۳۹۳). این قیمت = قیمت واحد برآوردی R02 بدون سربار؛ حمل، بیمه، ترخیص، سربار، مالیات و نصب شامل نیست.
Note on E148: ROT-FIR = Firewater & Safety Pumps آتش‌نشانی: پمپ اصلی برقی و دیزلی، Jockey و بارگیری آب آتش‌نشانی
Note on F148: BB (unspecified) – Between bearings – subtype not stated: منبع فقط «Between Bearings» گفته و زیرنوع API را مشخص نکرده
Note on G148: I-2: بدنه چدن، پروانه برنز؛ رینگ برنز؛ شفت فولاد کربنی. کاربرد معمول: آب، آب آتش‌نشانی و آب شیرین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N148: SOURCE – design code line "& IPS-M-PM-125" in the project item description
Note on O148: INFERRED – PC-ME 14040105 Pazanan2 PUMPS B24: no "NACE MR-0175" line in item description, while the document states it item-by-item where required → N
Note on S148: SOURCE – equipment name states electric motor driven
Note on Y148: SOURCE – PC-ME Cover D65: نسخه R02 = FEB 2015 (بهمن ۱۳۹۳)
Note on Z148: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR24
Note on AA148: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR24: R02 (1393) FOB unit price
Note on AF148: شرط تحویل: FOB (صریح؛ سرستون AR7 «Unit Price 'FOB' (€)»، نسخه R02 فوریه ۲۰۱۵ = بهمن ۱۳۹۳). این قیمت = قیمت واحد برآوردی R02 بدون سربار؛ حمل، بیمه، ترخیص، سربار، مالیات و نصب شامل نیست.
Note on E149: ROT-FIR = Firewater & Safety Pumps آتش‌نشانی: پمپ اصلی برقی و دیزلی، Jockey و بارگیری آب آتش‌نشانی
Note on F149: BB (unspecified) – Between bearings – subtype not stated: منبع فقط «Between Bearings» گفته و زیرنوع API را مشخص نکرده
Note on G149: I-2: بدنه چدن، پروانه برنز؛ رینگ برنز؛ شفت فولاد کربنی. کاربرد معمول: آب، آب آتش‌نشانی و آب شیرین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N149: SOURCE – design code line "& IPS-M-PM-125" in the project item description
Note on O149: INFERRED – PC-ME 14040105 Pazanan2 PUMPS B25: no "NACE MR-0175" line in item description, while the document states it item-by-item where required → N
Note on S149: SOURCE – equipment name states diesel engine driven
Note on Y149: SOURCE – PC-ME Cover D65: نسخه R02 = FEB 2015 (بهمن ۱۳۹۳)
Note on Z149: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR25
Note on AA149: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR25: R02 (1393) FOB unit price
Note on AF149: شرط تحویل: FOB (صریح؛ سرستون AR7 «Unit Price 'FOB' (€)»، نسخه R02 فوریه ۲۰۱۵ = بهمن ۱۳۹۳). این قیمت = قیمت واحد برآوردی R02 بدون سربار؛ حمل، بیمه، ترخیص، سربار، مالیات و نصب شامل نیست.
Note on E150: ROT-FIR = Firewater & Safety Pumps آتش‌نشانی: پمپ اصلی برقی و دیزلی، Jockey و بارگیری آب آتش‌نشانی
Note on F150: OH (unspecified) – Overhung – subtype not stated: منبع فقط «Overhung» گفته و زیرنوع API را مشخص نکرده
Note on G150: I-2: بدنه چدن، پروانه برنز؛ رینگ برنز؛ شفت فولاد کربنی. کاربرد معمول: آب، آب آتش‌نشانی و آب شیرین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on N150: SOURCE – design code line "& IPS-M-PM-125" in the project item description
Note on O150: INFERRED – PC-ME 14040105 Pazanan2 PUMPS B26: no "NACE MR-0175" line in item description, while the document states it item-by-item where required → N
Note on S150: INFERRED – نوع محرک در منبع ذکر نشده؛ موتور برقی فرض شده است
Note on Y150: SOURCE – PC-ME Cover D65: نسخه R02 = FEB 2015 (بهمن ۱۳۹۳)
Note on Z150: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR26
Note on AA150: SOURCE – PC-ME 14040105 Pazanan2 PUMPS AR26: R02 (1393) FOB unit price
Note on AF150: شرط تحویل: FOB (صریح؛ سرستون AR7 «Unit Price 'FOB' (€)»، نسخه R02 فوریه ۲۰۱۵ = بهمن ۱۳۹۳). این قیمت = قیمت واحد برآوردی R02 بدون سربار؛ حمل، بیمه، ترخیص، سربار، مالیات و نصب شامل نیست.

## Estimator
ESTIMATOR – برآورد قیمت پمپ جدید
پارامترهای زرد را انتخاب کنید؛ ضریب هر پارامتر در ستون C همان ردیف و محاسبات در پنل سمت راست بلافاصله به‌روز می‌شود. روش: میانگین Coef رکوردهای همتا × kW^n × ضرایب پیکربندی؛ سپس کف قیمت API 610.
پارامتر | مقدار | ضریب | محاسبه | نتیجه | توضیح
Sub-Category | ROT-INJ |  | Size driver kW | 217.9837 | kW یا Q·H/(367·η)
Only Match Sub-Category in peers? | Y |  | MAT_F | 1.9 | ضریب متریال
Pump Standard | API 610 |  | SEAL_F | 1.1648 | Arrangement × Category × Plan
Pump Family | Centrifugal |  | DRIVE_F | 1.05 | Driver × NACE
API 610 Type | BB3 |  | SCOPE_F | 1.02 | حاصل‌ضرب ۷ ضریب Scope
API 610 Material Class | D-2 | 1.9 | ALL_F | 2.3703 | ضریب کل پیکربندی
Seal Type / Arrangement | Arr 2 - Dual Unpressurized | 1.12 | Peer records (n) | 10 | رکوردهای همتای دارای Coef
API 682 Category | Cat 2 | 1 | Peer Coef – average | 9515.939 | EUR / kW^n، سال هدف، پیکربندی پایه
API 682 Seal Plan | 11+52 | 1.04 | Peer Coef – min | 5550.3244
Driver Type | Electric Motor | 1 | Peer Coef – max | 17266.6862
NACE MR0175 | Y | 1.05 | Floor applies? | Y | API 610، گریز از مرکز، کلاس S/D
Scope: Driver incl. | Y | 1 | Floor EUR (target year) | 25000 | ۲۵٬۰۰۰ یورو (۱۴۰۴) × نسبت PPI
Scope: Baseplate & Coupling | Y | 1 | نتیجه برآورد
Scope: Seal Support System | Y | 1 | Unit price EUR – expected | 570558.8376 | MAX(Coef میانگین × kW^n × ALL_F ، کف)
Scope: Comm. Spares | Y | 1 | Unit price EUR – low | 332787.6159 | با Coef کمینه همتاها
Scope: 2-yr Spares | N | 1 | Unit price EUR – high | 1035279.9024 | با Coef بیشینه همتاها
Scope: TPI | Y | 1.02 | Unit price USD – expected | 602386.3677 | × نرخ یورو ÷ نرخ دلار سال هدف
Scope: Witnessed FAT | N | 1 | Unit price IRR – expected | 396691301902.9551 | × نرخ یوروی سال هدف
Power (kW) – if known |  |  | Total IRR (× quantity) | 793382603805.9102
Capacity (m³/h) | 80 |  | Target year / EUR→IRR / USD→IRR | 1404 / 695,268 / 658,533 | از شیت Assumptions
Diff. Head (m) | 600
Quantity (sets) | 2

## Search
SEARCH – جستجوی بانک قیمت پمپ
(All) = بدون فیلتر؛ خانه خالی در بازه عددی = بدون محدودیت. نتایج با هر تغییر فوراً به‌روز می‌شوند (حداکثر ۲۰۰ ردیف).
فیلتر | مقدار |  | فیلتر | مقدار |  | فیلتر | مقدار | حداکثر
Text in Name / Tag |  |  | API 610 Type | (All) |  | Include in Totals | (All) | [16 empty] | 1 | 1
Project | (All) |  | Material Class | (All) |  | Only escalated price | N | [16 empty] | 1 | 2
Sub-Category | (All) |  | NACE MR0175 | (All) |  | Capacity m³/h (min / max) | [17 empty] | 1 | 3
Service Fluid | (All) |  | Seal Arrangement | (All) |  | Head m (min / max) | [17 empty] | 1 | 4
Pump Standard | (All) |  | Driver Type | (All) |  | Size kW (min / max) | [17 empty] | 1 | 5
Pump Family | (All) |  | Cost Year | (All) | [19 empty] | 1 | 6
[24 empty] | 1 | 7
تعداد نتایج | 146 |  | یورو تعدیل‌شده – کمینه | 3333.4351 |  | یورو تعدیل‌شده – میانگین | 67124.6687 | [16 empty] | 1 | 8
یورو تعدیل‌شده – بیشینه | 445018.3227 |  | ریال تعدیل‌شده – میانگین | 46669634160.7077 |  | سال هدف | 1404 | [16 empty] | 1 | 9
[24 empty] | 1 | 10
# | Master row | Row | Equipment Name | Project | Tag No. | Sub-Cat | API Type | Material | Q m³/h | Head m | Size kW | Standards | Seal | Driver | Service | Cost Year | Cur. | Unit Price (Ref) | Price Basis | Escalated EUR | Escalated USD | Escalated IRR | Incl. | 1 | 11
1 | 5 | 1 | 2nd Stage Separators Oil Pumps | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-CRU | Not stated | Not stated |  | 95.8 | 54.3 | Not stated | Not stated | Electric Motor | Crude Oil | (Not stated) | USD | 240000 | Purchase price (USD) – 18061405 pump CSV; project and year not stated | (PPI/FX missing) |  |  | N | 1 | 12
2 | 6 | 2 | 3rd Stage Separators Oil Pumps | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-CRU | Not stated | Not stated |  | 59.9 | 33.1 | Not stated | Not stated | Electric Motor | Crude Oil | (Not stated) | USD | 280000 | Purchase price (USD) – 18061405 pump CSV; project and year not stated | (PPI/FX missing) |  |  | N | 1 | 13
3 | 7 | 3 | Stabilized Oil Pump | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-CRU | Not stated | Not stated |  | 34.8 | 57.4 | Not stated | Not stated | Electric Motor | Crude Oil | (Not stated) | USD | 250000 | Purchase price (USD) – 18061405 pump CSV; project and year not stated | (PPI/FX missing) |  |  | N | 1 | 14
4 | 8 | 4 | Product Oil Pump | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-CRU | Not stated | Not stated |  | 329 | 379 | Not stated | Not stated | Electric Motor | Crude Oil | (Not stated) | USD | 420000 | Purchase price (USD) – 18061405 pump CSV; project and year not stated | (PPI/FX missing) |  |  | N | 1 | 15
5 | 9 | 5 | Off Spec Crude Pump | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-CRU | Not stated | Not stated |  | 311.3 | 48 | Not stated | Not stated | Electric Motor | Crude Oil | (Not stated) | USD | 75000 | Purchase price (USD) – 18061405 pump CSV; project and year not stated | (PPI/FX missing) |  |  | N | 1 | 16
6 | 10 | 6 | Second Stage Desalter Water Criculated Pump | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-WAT | Not stated | Not stated |  | 32 | 2.2 | Not stated | Not stated | Electric Motor | Process / Dilution Water | (Not stated) | USD | 60000 | Purchase price (USD) – 18061405 pump CSV; project and year not stated | (PPI/FX missing) |  |  | N | 1 | 17
7 | 11 | 7 | Degassing Water Pump | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-WAT | Not stated | Not stated |  | 36.2 | 13.1 | Not stated | Not stated | Electric Motor | Process / Dilution Water | (Not stated) | USD | 60000 | Purchase price (USD) – 18061405 pump CSV; project and year not stated | (PPI/FX missing) |  |  | N | 1 | 18
8 | 12 | 8 | Disposal Water Pump | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-INJ | Not stated | Not stated |  | 1383 | 423 | Not stated | Not stated | Electric Motor | Produced / Disposal Water | (Not stated) | USD | 410000 | Purchase price (USD) – 18061405 pump CSV; project and year not stated | (PPI/FX missing) |  |  | N | 1 | 19
9 | 13 | 9 | Fresh Water Pump | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-WAT | Not stated | Not stated |  | 41 | 3.9 | Not stated | Not stated | Electric Motor | Fresh / Potable Water | (Not stated) | USD | 8000 | Purchase price (USD) – 18061405 pump CSV; project and year not stated | (PPI/FX missing) |  |  | N | 1 | 20
10 | 14 | 10 | Closed Drain Pump | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-DRN | Not stated | Not stated |  | 120 | 13.7 | Not stated | Not stated | Electric Motor | Oily Water / Drain | (Not stated) | USD | 40000 | Purchase price (USD) – 18061405 pump CSV; project and year not stated | (PPI/FX missing) |  |  | N | 1 | 21
11 | 15 | 11 | Diesel Unlodaing pump | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-AUX | N/A (non-API 610) | Not stated |  | 27.2 | 4 | Not stated | Not stated | Electric Motor | Diesel / Fuel Oil | (Not stated) | USD | 5000 | Purchase price (USD) – 18061405 pump CSV; project and year not stated | (PPI/FX missing) |  |  | N | 1 | 22
12 | 16 | 12 | Diesel Transfer pump | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-AUX | N/A (non-API 610) | Not stated |  | 40.8 | 0.8 | Not stated | Not stated | Electric Motor | Diesel / Fuel Oil | (Not stated) | USD | 3000 | Purchase price (USD) – 18061405 pump CSV; project and year not stated | (PPI/FX missing) |  |  | N | 1 | 23
13 | 17 | 13 | Sludge Discharge Water Jet Pump | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-WAT | Not stated | Not stated |  | 15 | 5 | Not stated | Not stated | Electric Motor | Process / Dilution Water | (Not stated) | USD | 3000 | Purchase price (USD) – 18061405 pump CSV; project and year not stated | (PPI/FX missing) |  |  | N | 1 | 24
14 | 18 | 14 | Flare KO Drum Pumps | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | ROT-DRN | Not stated | Not stated |  | 18 | 2 | Not stated | Not stated | Electric Motor | Oily Water / Drain | (Not stated) | USD | 40000 | Purchase price (USD) – 18061405 pump CSV; project and year not stated | (PPI/FX missing) |  |  | N | 1 | 25
15 | 19 | 15 | MAIN TRANSFER PUMPS | Gachsaran 4 | P-001-A/B | ROT-CRU | Not stated | Not stated | 500 |  | 216.3 | Not stated | Not stated | Electric Motor | Crude Oil | 1402 | EUR | 385000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | 398446.6378 | 420673.219 | 277027196944.9313 | Y | 1 | 26
16 | 20 | 16 | AUXILLIARY TRANSFER PUMPS | Gachsaran 4 | P-002-A/B | ROT-CRU | Not stated | Not stated | 250 |  | 108.1 | Not stated | Not stated | Electric Motor | Crude Oil | 1402 | EUR | 135000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | 139715.0548 | 147508.7911 | 97139406720.9499 | Y | 1 | 27
17 | 21 | 17 | OFF-SPEC PUMPS | Gachsaran 4 | P-003-A/B | ROT-CRU | Not stated | Not stated | 100 |  | 44.2 | Not stated | Not stated | Electric Motor | Crude Oil | 1402 | EUR | 140000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | 144889.6865 | 152972.0796 | 100737162525.4296 | Y | 1 | 28
18 | 22 | 18 | DEGASSING WATER PUMPS | Gachsaran 4 | P-005-A/B | ROT-WAT | Not stated | Not stated | 30 |  | 2.7 | Not stated | Not stated | Electric Motor | Process / Dilution Water | 1402 | EUR | 34000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | 35187.4953 | 37150.3622 | 24464739470.4615 | Y | 1 | 29
19 | 23 | 19 | DILUTION WATER PUMPS | Gachsaran 4 | P-103 | ROT-WAT | Not stated | Not stated | 40 |  | 12 | Not stated | Not stated | Electric Motor | Process / Dilution Water | 1402 | EUR | 29000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | 30012.8636 | 31687.0736 | 20866983665.9818 | Y | 1 | 30
20 | 24 | 20 | DILUTION WATER PUMPS | Gachsaran 4 | P-106-A1/A2 | ROT-WAT | Not stated | Not stated | 20 |  | 6 | Not stated | Not stated | Electric Motor | Process / Dilution Water | 1402 | EUR | 27500 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | 28460.4741 | 30048.0871 | 19787656924.638 | Y | 1 | 31
21 | 25 | 21 | DEAERATED WATER PUMPS | Gachsaran 4 | P-102-A/B | ROT-WAT | Not stated | Not stated | 20 |  | 1.35 | Not stated | Not stated | Electric Motor | Deaerated Water | 1402 | EUR | 15000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | 15523.895 | 16389.8657 | 10793267413.4389 | Y | 1 | 32
22 | 26 | 22 | DEAERATED WATER PUMPS | Gachsaran 4 | P-105 | ROT-WAT | Not stated | Not stated | 40 |  | 2.7 | Not stated | Not stated | Electric Motor | Deaerated Water | 1402 | EUR | 17000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | 17593.7476 | 18575.1811 | 12232369735.2307 | Y | 1 | 33
23 | 27 | 23 | POTABLE WATER FILLING PUMP | Gachsaran 4 | P-104 | ROT-WAT | Not stated | Not stated | 20 |  | 1.4 | Not stated | Not stated | Electric Motor | Fresh / Potable Water | 1402 | EUR | 11000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | 11384.1897 | 12019.2348 | 7915062769.8552 | Y | 1 | 34
24 | 28 | 24 | WATER INJECTION MAIN PUMPS | Gachsaran 4 | P-201-A/B/C | ROT-INJ | Not stated | Not stated | 73 |  | 73.6 | Not stated | Not stated | Electric Motor | Produced / Disposal Water | 1402 | EUR | 430000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | 445018.3227 | 469842.8161 | 309406999185.2479 | Y | 1 | 35
25 | 29 | 25 | WATER INJECTION BOOSTER PUMPS | Gachsaran 4 | P-206-A/B/C | ROT-INJ | Not stated | Not stated | 36.5 |  | 36.5 | Not stated | Not stated | Electric Motor | Produced / Disposal Water | 1402 | EUR | 285000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | 294954.0046 | 311407.4479 | 205072080855.3387 | Y | 1 | 36
26 | 30 | 26 | CHEMICAL INJECTION PORTABLE PUMPS | Gachsaran 4 | P-501-A/B/C | ROT-AUX | Not stated | Not stated |  |  | 0.45 | Not stated | Not stated | Electric Motor | Chemical | 1402 | EUR | 9000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | 9314.337 | 9833.9194 | 6475960448.0633 | Y | 1 | 37
27 | 31 | 27 | FLARE K.O DRUM LIQUID PUMPS | Gachsaran 4 | P-601-A/B | ROT-DRN | Not stated | Not stated | 15 |  | 0.33 | Not stated | Not stated | Electric Motor | Oily Water / Drain | 1402 | EUR | 28000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | 28977.9373 | 30594.4159 | 20147432505.0859 | Y | 1 | 38
28 | 32 | 28 | HC CLOSED DRAIN TRANSFER PUMPS | Gachsaran 4 | P-701-A/B | ROT-DRN | Not stated | Not stated | 27.5 |  | 3.3 | Not stated | Not stated | Electric Motor | Oily Water / Drain | 1402 | EUR | 53000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | 54851.0956 | 57910.8587 | 38136211527.484 | Y | 1 | 39
29 | 33 | 29 | HC CLOSED DRAIN DRUM SUMP PUMP | Gachsaran 4 | P-702A/B | ROT-DRN | Not stated | Not stated | 5.5 |  | 0.11 | Not stated | Not stated | Electric Motor | Oily Water / Drain | 1402 | EUR | 53000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | 54851.0956 | 57910.8587 | 38136211527.484 | Y | 1 | 40
30 | 34 | 30 | CLEAN WATER PUMPS | Gachsaran 4 | P-703-A/B | ROT-WAT | Not stated | Not stated | 11 |  | 0.54 | Not stated | Not stated | Electric Motor | Process / Dilution Water | 1402 | EUR | 29000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | 30012.8636 | 31687.0736 | 20866983665.9818 | Y | 1 | 41
31 | 35 | 31 | RECOVERED WASTE OIL PUMPS | Gachsaran 4 | P-704-A/B | ROT-DRN | Not stated | Not stated | 11 |  | 0.8 | Not stated | Not stated | Electric Motor | Slop / Dirty Oil | 1402 | EUR | 35000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | 36222.4216 | 38243.0199 | 25184290631.3574 | Y | 1 | 42
32 | 36 | 32 | OILY WATER SEPARATOR PUMP | Gachsaran 4 | P-750 | ROT-DRN | Not stated | Not stated | 1 |  | 0.02 | Not stated | Not stated | Electric Motor | Oily Water / Drain | 1402 | EUR | 13350 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | 13816.2665 | 14586.9805 | 9606007997.9606 | Y | 1 | 43
33 | 37 | 33 | DIRTY OIL PUMPS | Gachsaran 4 | P-705-A/B | ROT-DRN | Not stated | Not stated | 5 |  | 0.3 | Not stated | Not stated | Electric Motor | Slop / Dirty Oil | 1402 | EUR | 31000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | 32082.7163 | 33872.3891 | 22306085987.7737 | Y | 1 | 44
34 | 38 | 34 | RECOVERED WASTE WATER PUMPS | Gachsaran 4 | P-706-A/B | ROT-INJ | Not stated | Not stated | 33 |  | 1.35 | Not stated | Not stated | Electric Motor | Produced / Disposal Water | 1402 | EUR | 28000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | 28977.9373 | 30594.4159 | 20147432505.0859 | Y | 1 | 45
35 | 39 | 35 | DIESEL OIL PUMP | Gachsaran 4 | P-801 | ROT-AUX | Not stated | Not stated | 10 |  | 0.16 | Not stated | Not stated | Electric Motor | Diesel / Fuel Oil | 1402 | EUR | 13500 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | 13971.5055 | 14750.8791 | 9713940672.095 | Y | 1 | 46
36 | 40 | 36 | FIRE WATER MAIN ELECTRICAL PUMP | Gachsaran 4 | P-901A/B | ROT-FIR | Not stated | Not stated | 480 |  | 133 | Not stated | Not stated | Electric Motor | Fire Water | 1402 | IRR | 37500000000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; IRR lump figure ¦ source label: AACE Class 2 | 73295.066 | 77383.6906 | 50959713944.4706 | Y | 1 | 47
37 | 41 | 37 | FIRE WATER MAIN DESEL PUMP | Gachsaran 4 | P902 | ROT-FIR | Not stated | Not stated | 480 |  | 133 | Not stated | Not stated | Diesel Engine | Fire Water | 1402 | IRR | 45000000000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; IRR lump figure ¦ source label: AACE Class 2 | 87954.0792 | 92860.4288 | 61151656733.3648 | Y | 1 | 48
38 | 42 | 38 | FIRE WATER JOCKEY PUMPS | Gachsaran 4 | P-903-A/B | ROT-FIR | Not stated | Not stated | 15 |  | 2.5 | Not stated | Not stated | Electric Motor | Fire Water | 1402 | IRR | 2000000000 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; IRR lump figure ¦ source label: AACE Class 2 | 3909.0702 | 4127.1302 | 2717851410.3718 | Y | 1 | 49
39 | 43 | 39 | UNIT SUPPLY WATER PUMP | Gachsaran 4 | P108A/B | ROT-WAT | Not stated | Not stated | 15 |  | 2.5 | Not stated | Not stated | Electric Motor | Fresh / Potable Water | 1402 | EUR | 17500 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | 18111.2108 | 19121.51 | 12592145315.6787 | Y | 1 | 50
40 | 44 | 40 | FIRE WATER LOADING PUMP | Gachsaran 4 | P-904 | ROT-FIR | Not stated | Not stated | 30 |  | 2.5 | Not stated | Not stated | Electric Motor | Fire Water | 1402 | EUR | 19500 | Consultant basic-design estimate – PEP Rev.1402/05, sheet P.ME «هزینه واحد بدون ضریب»; EUR figure (converted in the PEP at 420,000×1.085 IRR/EUR) ¦ source label: AACE Class 2 | 20181.0635 | 21306.8254 | 14031247637.4705 | Y | 1 | 51
41 | 45 | 41 | Salty Crude Transfer Pumps | Koopal Asmari | P-111 A/B/C | ROT-CRU | OH2 | D-1 | 354 | 31.2 | 50.158 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Crude Oil | 1393 | EUR | 55000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 74308.7348 | 78453.905 | 51664485443.8569 | Y | 1 | 52
42 | 46 | 42 | Salty Crude Booster Pumps | Koopal Asmari | P-114 A/B/C | ROT-CRU | OH2 | D-1 | 255 | 170 | 196.8665 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Crude Oil | 1393 | EUR | 60000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 81064.0744 | 85586.0782 | 56361256847.8439 | Y | 1 | 53
43 | 47 | 43 | Dirty Oil Pumps | Koopal Asmari | P-135 A/B | ROT-DRN | N/A (non-API 610) | D-1 | 5 |  |  | API 676 + IPS-M-PM-140 | Not stated | Electric Motor | Slop / Dirty Oil | 1393 | EUR | 10000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 13510.6791 | 14264.3464 | 9393542807.974 | Y | 1 | 54
44 | 48 | 44 | Free Water Transfer Pumps | Koopal Asmari | P-136 A/B | ROT-WAT | OH2 | D-2 | 21 | 27.6 | 2.6322 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Process / Dilution Water | 1393 | EUR | 30000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 40532.0372 | 42793.0391 | 28180628423.922 | Y | 1 | 55
45 | 49 | 45 | Disposal Water Injection Main Pumps | Koopal Asmari | P-137 A/B | ROT-INJ | BB3 | D-2 | 73 | 607.4 | 201.3633 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Produced / Disposal Water | 1393 | EUR | 210000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 283724.2602 | 299551.2738 | 197264398967.4538 | Y | 1 | 56
46 | 50 | 46 | Disposal Water Injection Booster Pumps | Koopal Asmari | P-139 A/B | ROT-INJ | BB3 | D-2 | 36 | 331 | 54.1144 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Produced / Disposal Water | 1393 | EUR | 150000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 202660.1859 | 213965.1955 | 140903142119.6099 | Y | 1 | 57
47 | 51 | 47 | Dilution Water Pumps | Koopal Asmari | P-151 A/B | ROT-WAT | OH2 | S-5 | 23 | 158 | 16.5032 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Process / Dilution Water | 1393 | EUR | 16500 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 25000 | 26394.577 | 17381700000 | Y | 1 | 58
48 | 52 | 48 | Dilution Water Pump | Koopal Asmari | P-152 | ROT-WAT | OH2 | S-5 | 43 | 158 | 30.8538 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Process / Dilution Water | 1393 | EUR | 17500 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 25000 | 26394.577 | 17381700000 | Y | 1 | 59
49 | 53 | 49 | Flare K.O. Drum Pumps | Koopal Asmari | P-171 A/B | ROT-DRN | OH2 | S-6 | 15 | 50 | 3.406 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Oily Water / Drain | 1393 | EUR | 10000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 25000 | 26394.577 | 17381700000 | Y | 1 | 60
50 | 54 | 50 | O.W.S. Oil Pumps | Koopal Asmari | P-231 A/B | ROT-DRN | N/A (non-API 610) | D-1 | 6 |  |  | API 676 + IPS-M-PM-140 | Not stated | Electric Motor | Slop / Dirty Oil | 1393 | EUR | 25000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 33776.6976 | 35660.8659 | 23483857019.935 | Y | 1 | 61
51 | 55 | 51 | O.W.S. Water Pumps | Koopal Asmari | P-232 A/B | ROT-WAT | OH2 | D-2 | 11 | 27.6 | 1.3787 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Oily Water / Drain | 1393 | EUR | 20000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 27021.3581 | 28528.6927 | 18787085615.948 | Y | 1 | 62
52 | 56 | 52 | Closed Drain Drum Pumps | Koopal Asmari | P-234 A/B | ROT-DRN | OH2 | D-2 | 15 | 46.81 | 3.1887 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Oily Water / Drain | 1393 | EUR | 15000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 25000 | 26394.577 | 17381700000 | Y | 1 | 63
53 | 57 | 53 | Desalters Recycle Pumps | Koopal Asmari | P-113 A/B | ROT-WAT | OH2 | D-2 | 21 | 44.9 | 4.282 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Process / Dilution Water | 1393 | IRR | (Not stated) | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); pump priced inside its package, no separate price ¦ source label: AACE Class 3 | (PPI/FX missing) |  |  | Y | 1 | 64
54 | 58 | 54 | IGF Water Recycle Pumps | Koopal Asmari | P-130 A/B | ROT-WAT | OH2 | D-2 |  |  |  | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Process / Dilution Water | 1393 | IRR | (Not stated) | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); pump priced inside its package, no separate price ¦ source label: AACE Class 3 | (PPI/FX missing) |  |  | Y | 1 | 65
55 | 59 | 55 | IGF De-oiled Waste Booster Pumps | Koopal Asmari | P-131 A/B | ROT-INJ | OH2 | D-2 |  |  |  | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Produced / Disposal Water | 1393 | IRR | (Not stated) | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); pump priced inside its package, no separate price ¦ source label: AACE Class 3 | (PPI/FX missing) |  |  | Y | 1 | 66
56 | 60 | 56 | IGF De-oiled Waste Booster Pumps | Koopal Asmari | P-132 A/B | ROT-INJ | OH2 | D-2 |  |  |  | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Produced / Disposal Water | 1393 | IRR | (Not stated) | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); pump priced inside its package, no separate price ¦ source label: AACE Class 3 | (PPI/FX missing) |  |  | Y | 1 | 67
57 | 61 | 57 | IGF Recovered Waste Oil Pumps | Koopal Asmari | P-133 A/B | ROT-DRN | N/A (non-API 610) | D-1 |  |  |  | API 676 + IPS-M-PM-140 | Not stated | Electric Motor | Slop / Dirty Oil | 1393 | IRR | (Not stated) | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); pump priced inside its package, no separate price ¦ source label: AACE Class 3 | (PPI/FX missing) |  |  | Y | 1 | 68
58 | 62 | 58 | IGF Oily Sludge Pumps | Koopal Asmari | P-134 A/B | ROT-DRN | N/A (non-API 610) | D-2 |  |  |  | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Sludge | 1393 | IRR | (Not stated) | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); pump priced inside its package, no separate price ¦ source label: AACE Class 3 | (PPI/FX missing) |  |  | Y | 1 | 69
59 | 63 | 59 | Salty Crude Transfer Pumps | Koopal Bangestan | P-121 A/B/C | ROT-CRU | OH2 | D-1 | 186 | 33.4 | 28.2125 | API 610 + IPS-G-PM-105 + NACE MR0175 | Not stated | Electric Motor | Crude Oil | 1393 | EUR | 55000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 74308.7348 | 78453.905 | 51664485443.8569 | Y | 1 | 70
60 | 64 | 60 | Off-Spec. Crude Pumps | Koopal Bangestan | P-122 A/B | ROT-CRU | OH2 | D-1 | 37 | 39 | 6.5531 | API 610 + IPS-G-PM-105 + NACE MR0175 | Not stated | Electric Motor | Crude Oil | 1393 | EUR | 15000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 25000 | 26394.577 | 17381700000 | Y | 1 | 71
61 | 65 | 61 | Salty Crude Booster Pumps | Koopal Bangestan | P-124 A/B/C | ROT-CRU | OH2 | D-1 | 173 | 186.3 | 146.3665 | API 610 + IPS-G-PM-105 + NACE MR0175 | Not stated | Electric Motor | Crude Oil | 1393 | EUR | 60000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 81064.0744 | 85586.0782 | 56361256847.8439 | Y | 1 | 72
62 | 66 | 62 | Dirty Oil Pumps | Koopal Bangestan | P-145 A/B | ROT-DRN | N/A (non-API 610) | D-1 | 5 |  |  | API 676 + IPS-M-PM-140 + NACE MR0175 | Not stated | Electric Motor | Slop / Dirty Oil | 1393 | EUR | 10000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 13510.6791 | 14264.3464 | 9393542807.974 | Y | 1 | 73
63 | 67 | 63 | Free Water Transfer Pumps | Koopal Bangestan | P-146 A/B | ROT-WAT | OH2 | D-2 | 14.5 | 27.6 | 1.8174 | API 610 + IPS-G-PM-105 + NACE MR0175 | Not stated | Electric Motor | Process / Dilution Water | 1393 | EUR | 35000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 47287.3767 | 49925.2123 | 32877399827.909 | Y | 1 | 74
64 | 68 | 64 | Disposal Water Injection Main Pumps | Koopal Bangestan | P-147 A/B | ROT-INJ | BB3 | D-2 | 44 | 670 | 133.8783 | API 610 + IPS-G-PM-105 + NACE MR0175 | Not stated | Electric Motor | Produced / Disposal Water | 1393 | EUR | 230000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 310745.6184 | 328079.9665 | 216051484583.4018 | Y | 1 | 75
65 | 69 | 65 | Disposal Water Injection Booster Pumps | Koopal Bangestan | P-149 A/B | ROT-INJ | BB3 | D-2 | 22 | 331 | 33.0699 | API 610 + IPS-G-PM-105 + NACE MR0175 | Not stated | Electric Motor | Produced / Disposal Water | 1393 | EUR | 160000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 216170.8649 | 228229.5419 | 150296684927.5838 | Y | 1 | 76
66 | 70 | 66 | Dilution Water Pumps | Koopal Bangestan | P-161 A/B | ROT-WAT | OH2 | S-5 | 19 | 168 | 14.4959 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Process / Dilution Water | 1393 | EUR | 16500 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 25000 | 26394.577 | 17381700000 | Y | 1 | 77
67 | 71 | 67 | Dilution Water Pump | Koopal Bangestan | P-162 | ROT-WAT | OH2 | S-5 | 33 | 168 | 25.1771 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Process / Dilution Water | 1393 | EUR | 17500 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 25000 | 26394.577 | 17381700000 | Y | 1 | 78
68 | 72 | 68 | Flare K.O. Drum Pumps | Koopal Bangestan | P-181 A/B | ROT-DRN | OH2 | S-6 | 15 | 52 | 3.5422 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Oily Water / Drain | 1393 | EUR | 10000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 25000 | 26394.577 | 17381700000 | Y | 1 | 79
69 | 73 | 69 | O.W.S. Oil Pumps | Koopal Bangestan | P-241 A/B | ROT-DRN | N/A (non-API 610) | D-1 | 5.5 |  |  | API 676 + IPS-M-PM-140 + NACE MR0175 | Not stated | Electric Motor | Slop / Dirty Oil | 1393 | EUR | 25000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 33776.6976 | 35660.8659 | 23483857019.935 | Y | 1 | 80
70 | 74 | 70 | O.W.S. Water Pumps | Koopal Bangestan | P-242 A/B | ROT-WAT | OH2 | D-2 | 11 | 28 | 1.3987 | API 610 + IPS-G-PM-105 + NACE MR0175 | Not stated | Electric Motor | Oily Water / Drain | 1393 | EUR | 20000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 27021.3581 | 28528.6927 | 18787085615.948 | Y | 1 | 81
71 | 75 | 71 | Closed Drain Drum Pumps | Koopal Bangestan | P-244 A/B | ROT-DRN | OH2 | D-2 | 15 | 61 | 4.1553 | API 610 + IPS-G-PM-105 + NACE MR0175 | Not stated | Electric Motor | Oily Water / Drain | 1393 | EUR | 17500 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 25000 | 26394.577 | 17381700000 | Y | 1 | 82
72 | 76 | 72 | Desalters Recycle Pumps | Koopal Bangestan | P-123 A/B | ROT-WAT | OH2 | D-2 | 15 | 44.9 | 3.0586 | API 610 + IPS-G-PM-105 + NACE MR0175 | Not stated | Electric Motor | Process / Dilution Water | 1393 | IRR | (Not stated) | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); pump priced inside its package, no separate price ¦ source label: AACE Class 3 | (PPI/FX missing) |  |  | Y | 1 | 83
73 | 77 | 73 | IGF Water Recycle Pumps | Koopal Bangestan | P-140 A/B | ROT-WAT | OH2 | D-2 |  |  |  | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Process / Dilution Water | 1393 | IRR | (Not stated) | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); pump priced inside its package, no separate price ¦ source label: AACE Class 3 | (PPI/FX missing) |  |  | Y | 1 | 84
74 | 78 | 74 | IGF De-oiled Waste Booster Pumps | Koopal Bangestan | P-141 A/B | ROT-INJ | OH2 | D-2 |  |  |  | API 610 + IPS-G-PM-105 + NACE MR0175 | Not stated | Electric Motor | Produced / Disposal Water | 1393 | IRR | (Not stated) | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); pump priced inside its package, no separate price ¦ source label: AACE Class 3 | (PPI/FX missing) |  |  | Y | 1 | 85
75 | 79 | 75 | IGF De-oiled Waste Booster Pumps | Koopal Bangestan | P-142 A/B | ROT-INJ | OH2 | D-2 |  |  |  | API 610 + IPS-G-PM-105 + NACE MR0175 | Not stated | Electric Motor | Produced / Disposal Water | 1393 | IRR | (Not stated) | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); pump priced inside its package, no separate price ¦ source label: AACE Class 3 | (PPI/FX missing) |  |  | Y | 1 | 86
76 | 80 | 76 | IGF Recovered Waste Oil Pumps | Koopal Bangestan | P-143 A/B | ROT-DRN | N/A (non-API 610) | D-1 |  |  |  | API 676 + IPS-M-PM-140 | Not stated | Electric Motor | Slop / Dirty Oil | 1393 | IRR | (Not stated) | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); pump priced inside its package, no separate price ¦ source label: AACE Class 3 | (PPI/FX missing) |  |  | Y | 1 | 87
77 | 81 | 77 | IGF Oily Sludge Pumps | Koopal Bangestan | P-144 A/B | ROT-DRN | N/A (non-API 610) | D-2 |  |  |  | API 610 + IPS-G-PM-105 + NACE MR0175 | Not stated | Electric Motor | Sludge | 1393 | IRR | (Not stated) | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); pump priced inside its package, no separate price ¦ source label: AACE Class 3 | (PPI/FX missing) |  |  | Y | 1 | 88
78 | 82 | 78 | Stripped Waste Water Pumps | Koopal Bangestan | P-148 A/B/C | ROT-INJ | OH2 | D-2 | 50 | 30.6 | 6.9482 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Produced / Disposal Water | 1393 | IRR | (Not stated) | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); pump priced inside its package, no separate price ¦ source label: AACE Class 3 | (PPI/FX missing) |  |  | Y | 1 | 89
79 | 83 | 79 | Deaerated Water Pumps | Koopal Asmari | P-153 A/B | ROT-WAT | N/A (non-API 610) | I-2 | 48 | 36 | 7.8474 | ISO 5199 + IPS-M-PM-115 | Not stated | Electric Motor | Deaerated Water | 1393 | EUR | 6500 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 8781.9414 | 9271.8251 | 6105802825.1831 | Y | 1 | 90
80 | 84 | 80 | Potable Water Loading Pumps | Koopal Asmari | P-158 | ROT-WAT | N/A (non-API 610) | I-2 | 33 | 31 | 4.6458 | ISO 5199 + IPS-M-PM-115 | Not stated | Electric Motor | Fresh / Potable Water | 1393 | EUR | 6500 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 8781.9414 | 9271.8251 | 6105802825.1831 | Y | 1 | 91
81 | 85 | 81 | Flare K.O. Drums Sump Pump | Koopal Asmari | P-172 | ROT-DRN | VS4 | S-6 | 5.5 | 43 | 1.074 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Oily Water / Drain | 1393 | EUR | 10000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 25000 | 26394.577 | 17381700000 | Y | 1 | 92
82 | 86 | 82 | Fuel Oil Pump | Koopal Asmari | P-201 | ROT-AUX | N/A (non-API 610) | S-1 | 10 | 41 | 1.8619 | ISO 5199 + IPS-M-PM-115 | Not stated | Electric Motor | Diesel / Fuel Oil | 1393 | EUR | 7000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 9457.4753 | 9985.0425 | 6575479965.5818 | Y | 1 | 93
83 | 87 | 83 | Closed Drain Drums Sump Pump | Koopal Asmari | P-235 | ROT-DRN | VS4 | S-6 | 5.5 | 31 | 0.7743 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Oily Water / Drain | 1393 | EUR | 10000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 25000 | 26394.577 | 17381700000 | Y | 1 | 94
84 | 88 | 84 | Fire Water Pump-Elect. Motor Driven | Koopal Asmari | P-270 | ROT-FIR | BB (unspecified) | I-2 | 770 | 107 | 374.1599 | NFPA 20 + IPS-M-PM-125 | Not stated | Electric Motor | Fire Water | 1393 | EUR | 70000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 94574.7534 | 99850.4246 | 65754799655.8179 | Y | 1 | 95
85 | 89 | 85 | Fire Water Pump-Diesel Engine Driven | Koopal Asmari | P-271 | ROT-FIR | BB (unspecified) | I-2 | 770 | 88.7 | 310.168 | NFPA 20 + IPS-M-PM-125 | Not stated | Diesel Engine | Fire Water | 1393 | EUR | 90000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 121596.1115 | 128379.1173 | 84541885271.7659 | Y | 1 | 96
86 | 90 | 86 | Fire Water Jockey Pumps | Koopal Asmari | P-272 A/B | ROT-FIR | OH (unspecified) | I-2 | 16.5 | 107 | 8.0177 | NFPA 20 + IPS-M-PM-125 | Not stated | Electric Motor | Fire Water | 1393 | EUR | 15000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 20266.0186 | 21396.5196 | 14090314211.961 | Y | 1 | 97
87 | 91 | 87 | Fire Water Loading Pump | Koopal Asmari | P-273 | ROT-FIR | N/A (non-API 610) | I-2 | 33 | 30.6 | 4.5858 | ISO 5199 + IPS-M-PM-115 | Not stated | Electric Motor | Fire Water | 1393 | EUR | 6500 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 8781.9414 | 9271.8251 | 6105802825.1831 | Y | 1 | 98
88 | 92 | 88 | Cooling Water (Sealing System) Recycle Pumps | Koopal Asmari | P-154 A/B | ROT-WAT | N/A (non-API 610) | I-2 | 3 | 30.6 | 0.41689 | ISO 5199 + IPS-M-PM-115 | Not stated | Electric Motor | Cooling / Seal Water | 1393 | IRR | 300000000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); local supplier price in IRR, before project overhead ¦ source label: AACE Class 3 | 10000.3052 | 10558.1531 | 6952892226.1396 | Y | 1 | 99
89 | 93 | 89 | Water Liquid Return Pumps (Deaeration System) | Koopal Asmari | P-157 A/B | ROT-WAT | N/A (non-API 610) | I-2 | 2 | 30.6 | 0.27793 | ISO 5199 + IPS-M-PM-115 | Not stated | Electric Motor | Cooling / Seal Water | 1393 | IRR | 250000000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); local supplier price in IRR, before project overhead ¦ source label: AACE Class 3 | 8333.5877 | 8798.4609 | 5794076855.1164 | Y | 1 | 100
90 | 94 | 90 | Evaporation Pond Portable Pump | Koopal Asmari | P-236 | ROT-INJ | N/A (non-API 610) | D-2 | 6 | 20.4 | 0.55586 | JIS B 8325 | Not stated | Electric Motor | Produced / Disposal Water | 1393 | EUR | 20000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 27021.3581 | 28528.6927 | 18787085615.948 | Y | 1 | 101
91 | 95 | 91 | Evaporation Pond Portable Pump | Koopal Bangestan | P-246 | ROT-INJ | N/A (non-API 610) | D-2 | 6 | 20.4 | 0.55586 | JIS B 8325 | Not stated | Electric Motor | Produced / Disposal Water | 1393 | EUR | 20000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); vendor-level price in EUR, before project overhead ¦ source label: AACE Class 3 | 27021.3581 | 28528.6927 | 18787085615.948 | Y | 1 | 102
92 | 96 | 92 | Chemical Loading Pumps | Koopal Asmari | P-220 A/B/C/D/E | ROT-AUX | N/A (non-API 610) | SS316L (non-API) | 9.6 |  |  | Not stated | Not stated | Electric Motor | Chemical | 1393 | IRR | 100000000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); local supplier price in IRR, before project overhead ¦ source label: AACE Class 3 | 3333.4351 | 3519.3844 | 2317630742.0465 | Y | 1 | 103
93 | 97 | 93 | Water Glycol Loading Pump | Koopal Asmari | P-116 | ROT-AUX | N/A (non-API 610) | SS316L (non-API) | 9.6 |  |  | Not stated | Not stated | Electric Motor | Chemical | 1393 | IRR | 100000000 | Consultant FEED MTO estimate – KPL-476 R03 (Jan 2016); local supplier price in IRR, before project overhead ¦ source label: AACE Class 3 | 3333.4351 | 3519.3844 | 2317630742.0465 | Y | 1 | 104
94 | 98 | 94 | Off Spec. Crude Pumps | Pazanan 2 | P-111 A/B | ROT-CRU | VS6 | D-1 | 45 | 139.1 | 28.4264 | API 610 + IPS-G-PM-105 + NACE MR0175 | Not stated | Electric Motor | Crude Oil | 1404 | EUR | 111500 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | 111500 | 117719.8136 | 77522382000 | Y | 1 | 105
95 | 99 | 95 | Deaerated Water Pumps | Pazanan 2 | P-122 A/B | ROT-WAT | N/A (non-API 610) | I-2 | 53 | 35.7 | 8.5926 | ISO 5199 + IPS-M-PM-115 | Not stated | Electric Motor | Deaerated Water | 1404 | EUR | 15050 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | 15050 | 15889.5354 | 10463783400 | Y | 1 | 106
96 | 100 | 96 | Dilution Water Pump | Pazanan 2 | P-124 | ROT-WAT | OH2 | I-2 | 53 | 122.3 | 29.4364 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Process / Dilution Water | 1404 | EUR | 22250 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | 22250 | 23491.1736 | 15469713000 | Y | 1 | 107
97 | 101 | 97 | Dilution Water Pumps | Pazanan 2 | P-125 A/B | ROT-WAT | OH2 | I-2 | 31 | 122 | 17.1753 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Process / Dilution Water | 1404 | EUR | 21500 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | 21500 | 22699.3363 | 14948262000 | Y | 1 | 108
98 | 102 | 98 | Disposal Water InjectionPumps | Pazanan 2 | P-136 A/B | ROT-INJ | BB3 | D-2 | 91 | 650 | 268.6194 | API 610 + IPS-G-PM-105 + NACE MR0175 | Not stated | Electric Motor | Produced / Disposal Water | 1404 | EUR | 317500 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | 317500 | 335211.1284 | 220747590000 | Y | 1 | 109
99 | 103 | 99 | Dirty Oil Pumps | Pazanan 2 | P-137 A/B | ROT-DRN | N/A (non-API 610) | D-1 | 5 |  |  | API 676 + IPS-M-PM-140 + NACE MR0175 | Not stated | Electric Motor | Slop / Dirty Oil | 1404 | EUR | 30000 | Vendor inquiry 1404Q1 – average of 1 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | 30000 | 31673.4924 | 20858040000 | Y | 1 | 110
100 | 104 | 100 | Evaporation Pond Water Return Pumps | Pazanan 2 | P-138 A/B | ROT-INJ | OH2 | D-2 | 15 | 27 | 1.8392 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Produced / Disposal Water | 1404 | EUR | 29000 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | 29000 | 30617.7094 | 20162772000 | Y | 1 | 111
101 | 105 | 101 | Disposal Water InjectionPumps | Pazanan 2 | P-139 A/B/C | ROT-INJ | BB3 | D-2 | 44 | 385 | 76.9301 | API 610 + IPS-G-PM-105 + NACE MR0175 | Not stated | Electric Motor | Produced / Disposal Water | 1404 | EUR | 247500 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | 247500 | 261306.3127 | 172078830000 | Y | 1 | 112
102 | 106 | 102 | Flare K.O. Drum Pumps | Pazanan 2 | P-151 A/B | ROT-DRN | OH2 | S-6 | 10 | 40 | 1.8165 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Oily Water / Drain | 1404 | EUR | 25500 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | 25500 | 26922.4686 | 17729334000 | Y | 1 | 113
103 | 107 | 103 | Closed Drain Drum Pumps | Pazanan 2 | P-161 A/B | ROT-DRN | OH2 | D-2 | 25 | 55 | 6.2443 | API 610 + IPS-G-PM-105 + NACE MR0175 | Not stated | Electric Motor | Oily Water / Drain | 1404 | EUR | 31000 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | 31000 | 32729.2755 | 21553308000 | Y | 1 | 114
104 | 108 | 104 | C. D. Drum / Flare K.O. Drum Sump Pump | Pazanan 2 | P-162 | ROT-DRN | VS4 | S-6 | 5 | 21.4 | 0.48592 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Oily Water / Drain | 1404 | EUR | 34500 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | 34500 | 36424.5163 | 23986746000 | Y | 1 | 115
105 | 109 | 105 | O.W.S. Oil Pumps | Pazanan 2 | P-163 A/B | ROT-DRN | N/A (non-API 610) | D-1 | 5 |  |  | API 676 + IPS-M-PM-140 + NACE MR0175 | Not stated | Electric Motor | Slop / Dirty Oil | 1393 | EUR | 25000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) – no 1404 quotation received (all vendors declined) | 33776.6976 | 35660.8659 | 23483857019.935 | Y | 1 | 116
106 | 110 | 106 | O.W.S. Water Pumps | Pazanan 2 | P-164 A/B | ROT-WAT | OH2 | D-2 | 15 | 50 | 3.406 | API 610 + IPS-G-PM-105 + NACE MR0175 | Not stated | Electric Motor | Oily Water / Drain | 1404 | EUR | 29600 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | 29600 | 31251.1792 | 20579932800 | Y | 1 | 117
107 | 111 | 107 | Oily Water Basin Pumps | Pazanan 2 | P-165 A/B | ROT-DRN | OH2 | S-6 | 15 | 20 | 1.3624 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Oily Water / Drain | 1404 | EUR | 26250 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | 26250 | 27714.3059 | 18250785000 | Y | 1 | 118
108 | 112 | 108 | Fuel Oil Pump | Pazanan 2 | P-171 | ROT-AUX | N/A (non-API 610) | S-1 | 10 | 21 | 0.95368 | ISO 5199 + IPS-M-PM-115 | Not stated | Electric Motor | Diesel / Fuel Oil | 1404 | EUR | 21000 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | 21000 | 22171.4447 | 14600628000 | Y | 1 | 119
109 | 113 | 109 | Fire Water Loading Pump | Pazanan 2 | P-191 | ROT-FIR | N/A (non-API 610) | I-2 | 33 | 31 | 4.6458 | ISO 5199 + IPS-M-PM-115 | Not stated | Electric Motor | Fire Water | 1404 | EUR | 16000 | Vendor inquiry 1404Q1 – average of 2 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | 16000 | 16892.5293 | 11124288000 | Y | 1 | 120
110 | 114 | 110 | Fire Water Pump-Elect. Motor Driven | Pazanan 2 | P-192 | ROT-FIR | BB (unspecified) | I-2 | 825 | 107 | 400.8856 | NFPA 20 + IPS-M-PM-125 | Not stated | Electric Motor | Fire Water | 1404 | EUR | 309660.11 | Vendor inquiry 1404Q1 – average of 3 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | 309660.11 | 326933.9051 | 215296765359.48 | Y | 1 | 121
111 | 115 | 111 | Fire Water Pump-Diesel Engine Driven | Pazanan 2 | P-193 | ROT-FIR | BB (unspecified) | I-2 | 825 | 107 | 400.8856 | NFPA 20 + IPS-M-PM-125 | Not stated | Diesel Engine | Fire Water | 1404 | EUR | 202973.76 | Vendor inquiry 1404Q1 – average of 3 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | 202973.76 | 214296.2618 | 141121160167.68 | Y | 1 | 122
112 | 116 | 112 | Fire Water Jockey Pumps | Pazanan 2 | P-194 A/B | ROT-FIR | OH (unspecified) | I-2 | 16.5 | 107 | 8.0177 | NFPA 20 + IPS-M-PM-125 | Not stated | Electric Motor | Fire Water | 1404 | EUR | 26808.07 | Vendor inquiry 1404Q1 – average of 3 quotation(s), PC-ME (91211-PZN-ME-RE-451) sheet PUMPS ¦ source label: AACE Class 1 | 26808.07 | 28303.5068 | 18638793212.76 | Y | 1 | 123
113 | 117 | 113 | Chemical Loading Pumps | Pazanan 2 | P-210 A/B | ROT-AUX | N/A (non-API 610) | SS316L (non-API) | 9.6 |  |  | Not stated | Not stated | Portable (Air / Electric) | Chemical | 1393 | IRR | 100000000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AQ (IRR) – no 1404 quotation received (all vendors declined) | 3333.4351 | 3519.3844 | 2317630742.0465 | Y | 1 | 124
114 | 118 | 114 | Chemical Loading Pumps | Pazanan 2 | P-211 | ROT-AUX | N/A (non-API 610) | SS316L (non-API) | 9.6 |  |  | Not stated | Not stated | Portable (Air / Electric) | Chemical | 1393 | IRR | 100000000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AQ (IRR) – no 1404 quotation received (all vendors declined) | 3333.4351 | 3519.3844 | 2317630742.0465 | Y | 1 | 125
115 | 119 | 115 | 2nd Stage Separators Oil Pumps | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-CRU | Not stated | Not stated |  | 95.8 | 54.3 | Not stated | Not stated | Electric Motor | Crude Oil | (Not stated) | USD | 580000 | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | (PPI/FX missing) |  |  | Y | 1 | 126
116 | 120 | 116 | 3rd Stage Separators Oil Pumps | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-CRU | Not stated | Not stated |  | 59.85 | 33.12 | Not stated | Not stated | Electric Motor | Crude Oil | (Not stated) | USD | 380000 | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | (PPI/FX missing) |  |  | Y | 1 | 127
117 | 121 | 117 | Stabilized Oil Pump | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-CRU | Not stated | Not stated |  | 34.75 | 57.35 | Not stated | Not stated | Electric Motor | Crude Oil | (Not stated) | USD | 250000 | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | (PPI/FX missing) |  |  | Y | 1 | 128
118 | 122 | 118 | Product Oil Pump | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-CRU | Not stated | Not stated |  |  |  | Not stated | Not stated | Electric Motor | Crude Oil | (Not stated) | USD | 320000 | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | (PPI/FX missing) |  |  | Y | 1 | 129
119 | 123 | 119 | Off Spec Crude Pump | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-CRU | Not stated | Not stated |  | 311.3 | 48 | Not stated | Not stated | Electric Motor | Crude Oil | (Not stated) | USD | 75000 | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | (PPI/FX missing) |  |  | Y | 1 | 130
120 | 124 | 120 | Second Stage Desalter Water Criculated Pump | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-WAT | Not stated | Not stated |  | 32 | 1 | Not stated | Not stated | Electric Motor | Process / Dilution Water | (Not stated) | USD | 60000 | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | (PPI/FX missing) |  |  | Y | 1 | 131
121 | 125 | 121 | Degassing Water Pump | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-WAT | Not stated | Not stated |  | 36.15 | 13.1 | Not stated | Not stated | Electric Motor | Process / Dilution Water | (Not stated) | USD | 60000 | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | (PPI/FX missing) |  |  | Y | 1 | 132
122 | 126 | 122 | Disposal Water Pump | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-INJ | Not stated | Not stated |  | 51.5 |  | Not stated | Not stated | Electric Motor | Produced / Disposal Water | (Not stated) | USD | 10000 | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | (PPI/FX missing) |  |  | Y | 1 | 133
123 | 127 | 123 | Fresh Water Pump | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-WAT | Not stated | Not stated |  | 41 | 3.9 | Not stated | Not stated | Electric Motor | Fresh / Potable Water | (Not stated) | USD | 8000 | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | (PPI/FX missing) |  |  | Y | 1 | 134
124 | 128 | 124 | Closed Drain Pump | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-DRN | Not stated | Not stated |  | 120 | 13.7 | Not stated | Not stated | Electric Motor | Oily Water / Drain | (Not stated) | USD | 40000 | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | (PPI/FX missing) |  |  | Y | 1 | 135
125 | 129 | 125 | Diesel Unlodaing pump | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-AUX | N/A (non-API 610) | Not stated |  | 27.2 |  | Not stated | Not stated | Not stated | Diesel / Fuel Oil | (Not stated) | USD | 5000 | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | (PPI/FX missing) |  |  | Y | 1 | 136
126 | 130 | 126 | Diesel Transfer pump | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-AUX | N/A (non-API 610) | Not stated |  | 40.8 | 0.83 | Not stated | Not stated | Electric Motor | Diesel / Fuel Oil | (Not stated) | USD | 3000 | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | (PPI/FX missing) |  |  | Y | 1 | 137
127 | 131 | 127 | Sludge Discharge Water Jet Pump | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-WAT | Not stated | Not stated |  |  |  | Not stated | Not stated | Electric Motor | Process / Dilution Water | (Not stated) | USD | 3000 | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | (PPI/FX missing) |  |  | Y | 1 | 138
128 | 132 | 128 | Flare KO Drum Pumps | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | ROT-DRN | Not stated | Not stated |  |  |  | Not stated | Not stated | Electric Motor | Oily Water / Drain | (Not stated) | USD | 40000 | Price (USD) – «نمونه قیمتی نمک‌زدایی» sheet PUMPS; project and year not stated | (PPI/FX missing) |  |  | Y | 1 | 139
129 | 133 | 129 | Off Spec. Crude Pumps | Pazanan 2 | P-111 A/B | ROT-CRU | VS6 | D-1 | 45 | 139.1 | 28.4264 | API 610 + IPS-G-PM-105 + NACE MR0175 | Not stated | Electric Motor | Crude Oil | 1393 | EUR | 75000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | 101330.0929 | 106982.5978 | 70451571059.8049 | Y | 1 | 140
130 | 134 | 130 | Deaerated Water Pumps | Pazanan 2 | P-122 A/B | ROT-WAT | N/A (non-API 610) | I-2 | 53 | 35.7 | 8.5926 | ISO 5199 + IPS-M-PM-115 | Not stated | Electric Motor | Deaerated Water | 1393 | EUR | 10000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | 13510.6791 | 14264.3464 | 9393542807.974 | Y | 1 | 141
131 | 135 | 131 | Dilution Water Pump | Pazanan 2 | P-124 | ROT-WAT | OH2 | I-2 | 53 | 122.3 | 29.4364 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Process / Dilution Water | 1393 | EUR | 15000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | 20266.0186 | 21396.5196 | 14090314211.961 | Y | 1 | 142
132 | 136 | 132 | Dilution Water Pumps | Pazanan 2 | P-125 A/B | ROT-WAT | OH2 | I-2 | 31 | 122 | 17.1753 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Process / Dilution Water | 1393 | EUR | 12000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | 16212.8149 | 17117.2156 | 11272251369.5688 | Y | 1 | 143
133 | 137 | 133 | Disposal Water InjectionPumps | Pazanan 2 | P-136 A/B | ROT-INJ | BB3 | D-2 | 91 | 650 | 268.6194 | API 610 + IPS-G-PM-105 + NACE MR0175 | Not stated | Electric Motor | Produced / Disposal Water | 1393 | EUR | 260000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | 351277.6555 | 370873.0056 | 244232113007.3237 | Y | 1 | 144
134 | 138 | 134 | Dirty Oil Pumps | Pazanan 2 | P-137 A/B | ROT-DRN | N/A (non-API 610) | D-1 | 5 |  |  | API 676 + IPS-M-PM-140 + NACE MR0175 | Not stated | Electric Motor | Slop / Dirty Oil | 1393 | EUR | 10000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | 13510.6791 | 14264.3464 | 9393542807.974 | Y | 1 | 145
135 | 139 | 135 | Evaporation Pond Water Return Pumps | Pazanan 2 | P-138 A/B | ROT-INJ | OH2 | D-2 | 15 | 27 | 1.8392 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Produced / Disposal Water | 1393 | EUR | 35000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | 47287.3767 | 49925.2123 | 32877399827.909 | Y | 1 | 146
136 | 140 | 136 | Disposal Water InjectionPumps | Pazanan 2 | P-139 A/B/C | ROT-INJ | BB3 | D-2 | 44 | 385 | 76.9301 | API 610 + IPS-G-PM-105 + NACE MR0175 | Not stated | Electric Motor | Produced / Disposal Water | 1393 | EUR | 180000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | 243192.2231 | 256758.2347 | 169083770543.5318 | Y | 0
137 | 141 | 137 | Flare K.O. Drum Pumps | Pazanan 2 | P-151 A/B | ROT-DRN | OH2 | S-6 | 10 | 40 | 1.8165 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Oily Water / Drain | 1393 | EUR | 15000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | 25000 | 26394.577 | 17381700000 | Y | 0
138 | 142 | 138 | Closed Drain Drum Pumps | Pazanan 2 | P-161 A/B | ROT-DRN | OH2 | D-2 | 25 | 55 | 6.2443 | API 610 + IPS-G-PM-105 + NACE MR0175 | Not stated | Electric Motor | Oily Water / Drain | 1393 | EUR | 32000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | 43234.173 | 45645.9084 | 30059336985.5168 | Y | 0
139 | 143 | 139 | C. D. Drum / Flare K.O. Drum Sump Pump | Pazanan 2 | P-162 | ROT-DRN | VS4 | S-6 | 5 | 21.4 | 0.48592 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Oily Water / Drain | 1393 | EUR | 15000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | 25000 | 26394.577 | 17381700000 | Y | 0
140 | 144 | 140 | O.W.S. Water Pumps | Pazanan 2 | P-164 A/B | ROT-WAT | OH2 | D-2 | 15 | 50 | 3.406 | API 610 + IPS-G-PM-105 + NACE MR0175 | Not stated | Electric Motor | Oily Water / Drain | 1393 | EUR | 15000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | 25000 | 26394.577 | 17381700000 | Y | 0
141 | 145 | 141 | Oily Water Basin Pumps | Pazanan 2 | P-165 A/B | ROT-DRN | OH2 | S-6 | 15 | 20 | 1.3624 | API 610 + IPS-G-PM-105 | Not stated | Electric Motor | Oily Water / Drain | 1393 | EUR | 15000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | 25000 | 26394.577 | 17381700000 | Y | 0
142 | 146 | 142 | Fuel Oil Pump | Pazanan 2 | P-171 | ROT-AUX | N/A (non-API 610) | S-1 | 10 | 21 | 0.95368 | ISO 5199 + IPS-M-PM-115 | Not stated | Electric Motor | Diesel / Fuel Oil | 1393 | EUR | 10000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | 13510.6791 | 14264.3464 | 9393542807.974 | Y | 0
143 | 147 | 143 | Fire Water Loading Pump | Pazanan 2 | P-191 | ROT-FIR | N/A (non-API 610) | I-2 | 33 | 31 | 4.6458 | ISO 5199 + IPS-M-PM-115 | Not stated | Electric Motor | Fire Water | 1393 | EUR | 6500 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | 8781.9414 | 9271.8251 | 6105802825.1831 | Y | 0
144 | 148 | 144 | Fire Water Pump-Elect. Motor Driven | Pazanan 2 | P-192 | ROT-FIR | BB (unspecified) | I-2 | 825 | 107 | 400.8856 | NFPA 20 + IPS-M-PM-125 | Not stated | Electric Motor | Fire Water | 1393 | EUR | 80000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | 108085.4325 | 114114.771 | 75148342463.7919 | Y | 0
145 | 149 | 145 | Fire Water Pump-Diesel Engine Driven | Pazanan 2 | P-193 | ROT-FIR | BB (unspecified) | I-2 | 825 | 107 | 400.8856 | NFPA 20 + IPS-M-PM-125 | Not stated | Diesel Engine | Fire Water | 1393 | EUR | 100000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | 135106.7906 | 142643.4637 | 93935428079.7399 | Y | 0
146 | 150 | 146 | Fire Water Jockey Pumps | Pazanan 2 | P-194 A/B | ROT-FIR | OH (unspecified) | I-2 | 16.5 | 107 | 8.0177 | NFPA 20 + IPS-M-PM-125 | Not stated | Electric Motor | Fire Water | 1393 | EUR | 15000 | Consultant basic MTO estimate R02 (Feb 2015), PC-ME sheet PUMPS col. AR (FOB EUR) | 20266.0186 | 21396.5196 | 14090314211.961 | Y | 0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0

## Vendor_Quotes
VENDOR_QUOTES – ثبت طولی استعلام‌ها (هر ردیف = یک پیشنهاد)
سند پیوست: در محاسبات Master استفاده نمی‌شود و فقط مبنای قیمت‌های استعلامی (مثل پازنان ۲، ۱۴۰۴) را مستند می‌کند. ستون Master Row = شماره Row رکورد در Master. ستون‌های (auto) خودکار پر می‌شوند. ردیف 5 نمونه است.
Quote_ID | Master Row | Tag (auto) | Equipment Name (auto) | Vendor_ID | Vendor Name (auto) | AVL Status (auto) | Quote Year (Jalali) | Quote Ref / Date | Validity (days) | Incoterm | Currency | Quoted Unit Price | TBE OK | Unit Price EUR (auto) | Delivery (weeks) | Sc: Driver | Sc: Baseplate | Sc: Seal System | Sc: Spares | Sc: TPI | Remarks
Q-EX01 | (e.g. 98) | — | — | V-EX01 | (Example vendor) | NIOC/NISOC Approved | 1404 | INQ-123 / 1404-02 | 90 | FOB | EUR | 317500 | Y | 317500 | 32 | Y | Y | Y | Y | N | نمونه – در شمارش وارد نمی‌شود
PZN2-P-111 A/B-V-01 | 94 | P-111 A/B | Off Spec. Crude Pumps | V-01 | آریا سپهر کیهان | Not checked | 1403 | 2025-02-15 |  | FOB | EUR | 43000 | Pending | 43000 | [6 empty] | Source: PUMPS I8:M8
PZN2-P-111 A/B-V-02 | 94 | P-111 A/B | Off Spec. Crude Pumps | V-02 | پمپیران | Not checked | 1404 | 2025-05-04 |  | FOB | EUR | 180000 | Pending | 180000 | [6 empty] | Source: PUMPS N8:R8
PZN2-P-111 A/B-V-03 | 94 | P-111 A/B | Off Spec. Crude Pumps | V-03 | کالای پمپ | Not checked | [14 empty] | Source: PUMPS S8:W8 – declined
PZN2-P-111 A/B-V-04 | 94 | P-111 A/B | Off Spec. Crude Pumps | V-04 | دالاهو پارس کیش (دمکو) | Not checked | [14 empty] | Source: PUMPS X8:AB8 – no reply
PZN2-P-122 A/B-V-01 | 95 | P-122 A/B | Deaerated Water Pumps | V-01 | آریا سپهر کیهان | Not checked | 1403 | 2025-02-15 |  | FOB | EUR | 14100 | Pending | 14100 | [6 empty] | Source: PUMPS I9:M9
PZN2-P-122 A/B-V-02 | 95 | P-122 A/B | Deaerated Water Pumps | V-02 | پمپیران | Not checked | 1404 | 2025-05-04 |  | FOB | EUR | 16000 | Pending | 16000 | [6 empty] | Source: PUMPS N9:R9
PZN2-P-122 A/B-V-03 | 95 | P-122 A/B | Deaerated Water Pumps | V-03 | کالای پمپ | Not checked | [14 empty] | Source: PUMPS S9:W9 – declined
PZN2-P-122 A/B-V-04 | 95 | P-122 A/B | Deaerated Water Pumps | V-04 | دالاهو پارس کیش (دمکو) | Not checked | [14 empty] | Source: PUMPS X9:AB9 – no reply
PZN2-P-124-V-01 | 96 | P-124 | Dilution Water Pump | V-01 | آریا سپهر کیهان | Not checked | 1403 | 2025-02-15 |  | FOB | EUR | 28500 | Pending | 28500 | [6 empty] | Source: PUMPS I10:M10
PZN2-P-124-V-02 | 96 | P-124 | Dilution Water Pump | V-02 | پمپیران | Not checked | 1404 | 2025-05-04 |  | FOB | EUR | 16000 | Pending | 16000 | [6 empty] | Source: PUMPS N10:R10
PZN2-P-124-V-03 | 96 | P-124 | Dilution Water Pump | V-03 | کالای پمپ | Not checked | [14 empty] | Source: PUMPS S10:W10 – declined
PZN2-P-124-V-04 | 96 | P-124 | Dilution Water Pump | V-04 | دالاهو پارس کیش (دمکو) | Not checked | [14 empty] | Source: PUMPS X10:AB10 – no reply
PZN2-P-125 A/B-V-01 | 97 | P-125 A/B | Dilution Water Pumps | V-01 | آریا سپهر کیهان | Not checked | 1403 | 2025-02-15 |  | FOB | EUR | 27000 | Pending | 27000 | [6 empty] | Source: PUMPS I11:M11
PZN2-P-125 A/B-V-02 | 97 | P-125 A/B | Dilution Water Pumps | V-02 | پمپیران | Not checked | 1404 | 2025-05-04 |  | FOB | EUR | 16000 | Pending | 16000 | [6 empty] | Source: PUMPS N11:R11
PZN2-P-125 A/B-V-03 | 97 | P-125 A/B | Dilution Water Pumps | V-03 | کالای پمپ | Not checked | [14 empty] | Source: PUMPS S11:W11 – declined
PZN2-P-125 A/B-V-04 | 97 | P-125 A/B | Dilution Water Pumps | V-04 | دالاهو پارس کیش (دمکو) | Not checked | [14 empty] | Source: PUMPS X11:AB11 – no reply
PZN2-P-136 A/B-V-01 | 98 | P-136 A/B | Disposal Water InjectionPumps | V-01 | آریا سپهر کیهان | Not checked | 1403 | 2025-02-15 |  | FOB | EUR | 335000 | Pending | 335000 | [6 empty] | Source: PUMPS I12:M12
PZN2-P-136 A/B-V-02 | 98 | P-136 A/B | Disposal Water InjectionPumps | V-02 | پمپیران | Not checked | 1404 | 2025-05-04 |  | FOB | EUR | 300000 | Pending | 300000 | [6 empty] | Source: PUMPS N12:R12
PZN2-P-136 A/B-V-03 | 98 | P-136 A/B | Disposal Water InjectionPumps | V-03 | کالای پمپ | Not checked | [14 empty] | Source: PUMPS S12:W12 – declined
PZN2-P-136 A/B-V-04 | 98 | P-136 A/B | Disposal Water InjectionPumps | V-04 | دالاهو پارس کیش (دمکو) | Not checked | [14 empty] | Source: PUMPS X12:AB12 – no reply
PZN2-P-137 A/B-V-01 | 99 | P-137 A/B | Dirty Oil Pumps | V-01 | آریا سپهر کیهان | Not checked | 1403 | 2025-02-15 |  | FOB | EUR | 30000 | Pending | 30000 | [6 empty] | Source: PUMPS I13:M13
PZN2-P-137 A/B-V-02 | 99 | P-137 A/B | Dirty Oil Pumps | V-02 | پمپیران | Not checked | [14 empty] | Source: PUMPS N13:R13 – declined
PZN2-P-137 A/B-V-03 | 99 | P-137 A/B | Dirty Oil Pumps | V-03 | کالای پمپ | Not checked | [14 empty] | Source: PUMPS S13:W13 – declined
PZN2-P-137 A/B-V-04 | 99 | P-137 A/B | Dirty Oil Pumps | V-04 | دالاهو پارس کیش (دمکو) | Not checked | [14 empty] | Source: PUMPS X13:AB13 – no reply
PZN2-P-138 A/B-V-01 | 100 | P-138 A/B | Evaporation Pond Water Return Pumps | V-01 | آریا سپهر کیهان | Not checked | 1403 | 2025-02-15 |  | FOB | EUR | 28000 | Pending | 28000 | [6 empty] | Source: PUMPS I14:M14
PZN2-P-138 A/B-V-02 | 100 | P-138 A/B | Evaporation Pond Water Return Pumps | V-02 | پمپیران | Not checked | 1404 | 2025-05-04 |  | FOB | EUR | 30000 | Pending | 30000 | [6 empty] | Source: PUMPS N14:R14
PZN2-P-138 A/B-V-03 | 100 | P-138 A/B | Evaporation Pond Water Return Pumps | V-03 | کالای پمپ | Not checked | [14 empty] | Source: PUMPS S14:W14 – declined
PZN2-P-138 A/B-V-04 | 100 | P-138 A/B | Evaporation Pond Water Return Pumps | V-04 | دالاهو پارس کیش (دمکو) | Not checked | [14 empty] | Source: PUMPS X14:AB14 – no reply
PZN2-P-139 A/B/C-V-01 | 101 | P-139 A/B/C | Disposal Water InjectionPumps | V-01 | آریا سپهر کیهان | Not checked | 1403 | 2025-02-15 |  | FOB | EUR | 225000 | Pending | 225000 | [6 empty] | Source: PUMPS I15:M15
PZN2-P-139 A/B/C-V-02 | 101 | P-139 A/B/C | Disposal Water InjectionPumps | V-02 | پمپیران | Not checked | 1404 | 2025-05-04 |  | FOB | EUR | 270000 | Pending | 270000 | [6 empty] | Source: PUMPS N15:R15
PZN2-P-139 A/B/C-V-03 | 101 | P-139 A/B/C | Disposal Water InjectionPumps | V-03 | کالای پمپ | Not checked | [14 empty] | Source: PUMPS S15:W15 – declined
PZN2-P-139 A/B/C-V-04 | 101 | P-139 A/B/C | Disposal Water InjectionPumps | V-04 | دالاهو پارس کیش (دمکو) | Not checked | [14 empty] | Source: PUMPS X15:AB15 – no reply
PZN2-P-151 A/B-V-01 | 102 | P-151 A/B | Flare K.O. Drum Pumps | V-01 | آریا سپهر کیهان | Not checked | 1403 | 2025-02-15 |  | FOB | EUR | 21000 | Pending | 21000 | [6 empty] | Source: PUMPS I16:M16
PZN2-P-151 A/B-V-02 | 102 | P-151 A/B | Flare K.O. Drum Pumps | V-02 | پمپیران | Not checked | 1404 | 2025-05-04 |  | FOB | EUR | 30000 | Pending | 30000 | [6 empty] | Source: PUMPS N16:R16
PZN2-P-151 A/B-V-03 | 102 | P-151 A/B | Flare K.O. Drum Pumps | V-03 | کالای پمپ | Not checked | [14 empty] | Source: PUMPS S16:W16 – declined
PZN2-P-151 A/B-V-04 | 102 | P-151 A/B | Flare K.O. Drum Pumps | V-04 | دالاهو پارس کیش (دمکو) | Not checked | [14 empty] | Source: PUMPS X16:AB16 – no reply
PZN2-P-161 A/B-V-01 | 103 | P-161 A/B | Closed Drain Drum Pumps | V-01 | آریا سپهر کیهان | Not checked | 1403 | 2025-02-15 |  | FOB | EUR | 32000 | Pending | 32000 | [6 empty] | Source: PUMPS I17:M17
PZN2-P-161 A/B-V-02 | 103 | P-161 A/B | Closed Drain Drum Pumps | V-02 | پمپیران | Not checked | 1404 | 2025-05-04 |  | FOB | EUR | 30000 | Pending | 30000 | [6 empty] | Source: PUMPS N17:R17
PZN2-P-161 A/B-V-03 | 103 | P-161 A/B | Closed Drain Drum Pumps | V-03 | کالای پمپ | Not checked | [14 empty] | Source: PUMPS S17:W17 – declined
PZN2-P-161 A/B-V-04 | 103 | P-161 A/B | Closed Drain Drum Pumps | V-04 | دالاهو پارس کیش (دمکو) | Not checked | [14 empty] | Source: PUMPS X17:AB17 – no reply
PZN2-P-162-V-01 | 104 | P-162 | C. D. Drum / Flare K.O. Drum Sump Pump | V-01 | آریا سپهر کیهان | Not checked | 1403 | 2025-02-15 |  | FOB | EUR | 24000 | Pending | 24000 | [6 empty] | Source: PUMPS I18:M18
PZN2-P-162-V-02 | 104 | P-162 | C. D. Drum / Flare K.O. Drum Sump Pump | V-02 | پمپیران | Not checked | 1404 | 2025-05-04 |  | FOB | EUR | 45000 | Pending | 45000 | [6 empty] | Source: PUMPS N18:R18
PZN2-P-162-V-03 | 104 | P-162 | C. D. Drum / Flare K.O. Drum Sump Pump | V-03 | کالای پمپ | Not checked | [14 empty] | Source: PUMPS S18:W18 – declined
PZN2-P-162-V-04 | 104 | P-162 | C. D. Drum / Flare K.O. Drum Sump Pump | V-04 | دالاهو پارس کیش (دمکو) | Not checked | [14 empty] | Source: PUMPS X18:AB18 – no reply
PZN2-P-163 A/B-V-01 | 105 | P-163 A/B | O.W.S. Oil Pumps | V-01 | آریا سپهر کیهان | Not checked | [14 empty] | Source: PUMPS I19:M19 – declined
PZN2-P-163 A/B-V-02 | 105 | P-163 A/B | O.W.S. Oil Pumps | V-02 | پمپیران | Not checked | [14 empty] | Source: PUMPS N19:R19 – declined
PZN2-P-163 A/B-V-03 | 105 | P-163 A/B | O.W.S. Oil Pumps | V-03 | کالای پمپ | Not checked | [14 empty] | Source: PUMPS S19:W19 – declined
PZN2-P-163 A/B-V-04 | 105 | P-163 A/B | O.W.S. Oil Pumps | V-04 | دالاهو پارس کیش (دمکو) | Not checked | [14 empty] | Source: PUMPS X19:AB19 – no reply
PZN2-P-164 A/B-V-01 | 106 | P-164 A/B | O.W.S. Water Pumps | V-01 | آریا سپهر کیهان | Not checked | 1403 | 2025-02-15 |  | FOB | EUR | 29200 | Pending | 29200 | [6 empty] | Source: PUMPS I20:M20
PZN2-P-164 A/B-V-02 | 106 | P-164 A/B | O.W.S. Water Pumps | V-02 | پمپیران | Not checked | 1404 | 2025-05-04 |  | FOB | EUR | 30000 | Pending | 30000 | [6 empty] | Source: PUMPS N20:R20
PZN2-P-164 A/B-V-03 | 106 | P-164 A/B | O.W.S. Water Pumps | V-03 | کالای پمپ | Not checked | [14 empty] | Source: PUMPS S20:W20 – declined
PZN2-P-164 A/B-V-04 | 106 | P-164 A/B | O.W.S. Water Pumps | V-04 | دالاهو پارس کیش (دمکو) | Not checked | [14 empty] | Source: PUMPS X20:AB20 – no reply
PZN2-P-165 A/B-V-01 | 107 | P-165 A/B | Oily Water Basin Pumps | V-01 | آریا سپهر کیهان | Not checked | 1403 | 2025-02-15 |  | FOB | EUR | 22500 | Pending | 22500 | [6 empty] | Source: PUMPS I21:M21
PZN2-P-165 A/B-V-02 | 107 | P-165 A/B | Oily Water Basin Pumps | V-02 | پمپیران | Not checked | 1404 | 2025-05-04 |  | FOB | EUR | 30000 | Pending | 30000 | [6 empty] | Source: PUMPS N21:R21
PZN2-P-165 A/B-V-03 | 107 | P-165 A/B | Oily Water Basin Pumps | V-03 | کالای پمپ | Not checked | [14 empty] | Source: PUMPS S21:W21 – declined
PZN2-P-165 A/B-V-04 | 107 | P-165 A/B | Oily Water Basin Pumps | V-04 | دالاهو پارس کیش (دمکو) | Not checked | [14 empty] | Source: PUMPS X21:AB21 – no reply
PZN2-P-171-V-01 | 108 | P-171 | Fuel Oil Pump | V-01 | آریا سپهر کیهان | Not checked | 1403 | 2025-02-15 |  | FOB | EUR | 12000 | Pending | 12000 | [6 empty] | Source: PUMPS I22:M22
PZN2-P-171-V-02 | 108 | P-171 | Fuel Oil Pump | V-02 | پمپیران | Not checked | 1404 | 2025-05-04 |  | FOB | EUR | 30000 | Pending | 30000 | [6 empty] | Source: PUMPS N22:R22
PZN2-P-171-V-03 | 108 | P-171 | Fuel Oil Pump | V-03 | کالای پمپ | Not checked | [14 empty] | Source: PUMPS S22:W22 – declined
PZN2-P-171-V-04 | 108 | P-171 | Fuel Oil Pump | V-04 | دالاهو پارس کیش (دمکو) | Not checked | [14 empty] | Source: PUMPS X22:AB22 – no reply
PZN2-P-191-V-01 | 109 | P-191 | Fire Water Loading Pump | V-01 | آریا سپهر کیهان | Not checked | 1403 | 2025-02-15 |  | FOB | EUR | 19000 | Pending | 19000 | [6 empty] | Source: PUMPS I23:M23
PZN2-P-191-V-02 | 109 | P-191 | Fire Water Loading Pump | V-02 | پمپیران | Not checked | 1404 | 2025-05-04 |  | FOB | EUR | 13000 | Pending | 13000 | [6 empty] | Source: PUMPS N23:R23
PZN2-P-191-V-03 | 109 | P-191 | Fire Water Loading Pump | V-03 | کالای پمپ | Not checked | [14 empty] | Source: PUMPS S23:W23 – declined
PZN2-P-191-V-04 | 109 | P-191 | Fire Water Loading Pump | V-04 | دالاهو پارس کیش (دمکو) | Not checked | [14 empty] | Source: PUMPS X23:AB23 – no reply
PZN2-P-192-V-01 | 110 | P-192 | Fire Water Pump-Elect. Motor Driven | V-01 | آریا سپهر کیهان | Not checked | 1403 | 2025-02-15 |  | FOB | EUR | 200000 | Pending | 200000 | [6 empty] | Source: PUMPS I24:M24
PZN2-P-192-V-02 | 110 | P-192 | Fire Water Pump-Elect. Motor Driven | V-02 | پمپیران | Not checked | 1404 | 2025-05-04 |  | FOB | EUR | 30000 | Pending | 30000 | [6 empty] | Source: PUMPS N24:R24
PZN2-P-192-V-03 | 110 | P-192 | Fire Water Pump-Elect. Motor Driven | V-03 | کالای پمپ | Not checked | 1403 | 2025-02-21 |  | FOB | EUR | 698980.33 | Pending | 698980.33 | [6 empty] | Source: PUMPS S24:W24
PZN2-P-192-V-04 | 110 | P-192 | Fire Water Pump-Elect. Motor Driven | V-04 | دالاهو پارس کیش (دمکو) | Not checked | [14 empty] | Source: PUMPS X24:AB24 – no reply
PZN2-P-193-V-01 | 111 | P-193 | Fire Water Pump-Diesel Engine Driven | V-01 | آریا سپهر کیهان | Not checked | 1403 | 2025-02-15 |  | FOB | EUR | 225000 | Pending | 225000 | [6 empty] | Source: PUMPS I25:M25
PZN2-P-193-V-02 | 111 | P-193 | Fire Water Pump-Diesel Engine Driven | V-02 | پمپیران | Not checked | 1404 | 2025-05-04 |  | FOB | EUR | 120000 | Pending | 120000 | [6 empty] | Source: PUMPS N25:R25
PZN2-P-193-V-03 | 111 | P-193 | Fire Water Pump-Diesel Engine Driven | V-03 | کالای پمپ | Not checked | 1403 | 2025-02-21 |  | FOB | EUR | 263921.27 | Pending | 263921.27 | [6 empty] | Source: PUMPS S25:W25
PZN2-P-193-V-04 | 111 | P-193 | Fire Water Pump-Diesel Engine Driven | V-04 | دالاهو پارس کیش (دمکو) | Not checked | [14 empty] | Source: PUMPS X25:AB25 – no reply
PZN2-P-194 A/B-V-01 | 112 | P-194 A/B | Fire Water Jockey Pumps | V-01 | آریا سپهر کیهان | Not checked | 1403 | 2025-02-15 |  | FOB | EUR | 19000 | Pending | 19000 | [6 empty] | Source: PUMPS I26:M26
PZN2-P-194 A/B-V-02 | 112 | P-194 A/B | Fire Water Jockey Pumps | V-02 | پمپیران | Not checked | 1404 | 2025-05-04 |  | FOB | EUR | 21000 | Pending | 21000 | [6 empty] | Source: PUMPS N26:R26
PZN2-P-194 A/B-V-03 | 112 | P-194 A/B | Fire Water Jockey Pumps | V-03 | کالای پمپ | Not checked | 1403 | 2025-02-21 |  | FOB | EUR | 40424.2 | Pending | 40424.2 | [6 empty] | Source: PUMPS S26:W26
PZN2-P-194 A/B-V-04 | 112 | P-194 A/B | Fire Water Jockey Pumps | V-04 | دالاهو پارس کیش (دمکو) | Not checked | [14 empty] | Source: PUMPS X26:AB26 – no reply
PZN2-P-210 A/B-V-01 | 113 | P-210 A/B | Chemical Loading Pumps | V-01 | آریا سپهر کیهان | Not checked | [14 empty] | Source: PUMPS I27:M27 – declined
PZN2-P-210 A/B-V-02 | 113 | P-210 A/B | Chemical Loading Pumps | V-02 | پمپیران | Not checked | [14 empty] | Source: PUMPS N27:R27 – declined
PZN2-P-210 A/B-V-03 | 113 | P-210 A/B | Chemical Loading Pumps | V-03 | کالای پمپ | Not checked | [14 empty] | Source: PUMPS S27:W27 – declined
PZN2-P-210 A/B-V-04 | 113 | P-210 A/B | Chemical Loading Pumps | V-04 | دالاهو پارس کیش (دمکو) | Not checked | [14 empty] | Source: PUMPS X27:AB27 – no reply
PZN2-P-211-V-01 | 114 | P-211 | Chemical Loading Pumps | V-01 | آریا سپهر کیهان | Not checked | [14 empty] | Source: PUMPS I28:M28 – declined
PZN2-P-211-V-02 | 114 | P-211 | Chemical Loading Pumps | V-02 | پمپیران | Not checked | [14 empty] | Source: PUMPS N28:R28 – declined
PZN2-P-211-V-03 | 114 | P-211 | Chemical Loading Pumps | V-03 | کالای پمپ | Not checked | [14 empty] | Source: PUMPS S28:W28 – declined
PZN2-P-211-V-04 | 114 | P-211 | Chemical Loading Pumps | V-04 | دالاهو پارس کیش (دمکو) | Not checked | [14 empty] | Source: PUMPS X28:AB28 – no reply
Note on K6: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K7: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K10: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K11: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K14: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K15: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K18: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K19: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K22: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K23: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K26: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K30: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K31: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K34: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K35: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K38: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K39: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K42: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K43: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K46: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K47: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K54: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K55: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K58: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K59: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K62: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K63: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K66: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K67: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K70: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K71: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K72: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K74: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K75: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K76: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K78: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K79: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB
Note on K80: INFERRED – column header F7 "GOING UNIT PRICE FOB EUR 1404Q1" (average of these quotes) → quotes taken as FOB

## Vendor_Register
VENDOR_REGISTER – فهرست سازندگان و وضعیت AVL
ردیف 5 نمونه است (خاکستری). ردیف‌های بعدی را تکمیل کنید؛ Vendor_ID در Master و Vendor_Quotes به‌صورت Dropdown از ستون A خوانده می‌شود.
Vendor_ID | Vendor Name | Country | Origin | AVL_Status | Vendor_Rank | Pump types supplied | Licensor / OEM | Notes
V-EX01 | (Example vendor) | Iran | Domestic (Licensed) | NIOC/NISOC Approved | Rank 1 | API 610 OH2/BB2 | (Licensor name) | نمونه – حذف یا جایگزین کنید
V-01 | آریا سپهر کیهان | Iran |  | Not checked |  |  |  | Pazanan 2 pump inquiries (PC-ME 14040105, sheet PUMPS, cols I:AG)
V-02 | پمپیران | Iran |  | Not checked |  |  |  | Pazanan 2 pump inquiries (PC-ME 14040105, sheet PUMPS, cols I:AG)
V-03 | کالای پمپ | Iran |  | Not checked |  |  |  | Pazanan 2 pump inquiries (PC-ME 14040105, sheet PUMPS, cols I:AG)
V-04 | دالاهو پارس کیش (دمکو) | Iran |  | Not checked |  |  |  | Pazanan 2 pump inquiries (PC-ME 14040105, sheet PUMPS, cols I:AG)

## Factors_ROT
FACTORS_ROT – ضرایب نرمال‌سازی (پیکربندی پایه: S-5، Seal Arr 1 / Plan 11 / Cat 2، موتور برقی، بدون NACE، Scope پایه)
ستون D ضریب اولیه بر پایه قضاوت مهندسی است و کالیبره نشده. ضریب کالیبره را در ستون E (زرد) وارد کنید؛ ستون F خودکار جایگزین می‌شود.
Key | Group | Option | Provisional Factor | Calibrated Factor (input) | Used Factor | Status | Description
MAT¦I-1 | MAT | I-1 | 0.75 |  | 0.75 | Provisional – calibrate | API 610 material class – base S-5 = 1.00 ¦ بدنه چدن، پروانه چدن؛ رینگ چدن؛ شفت فولاد کربنی
MAT¦I-2 | MAT | I-2 | 0.8 |  | 0.8 | Provisional – calibrate | API 610 material class – base S-5 = 1.00 ¦ بدنه چدن، پروانه برنز؛ رینگ برنز؛ شفت فولاد کربنی
MAT¦S-1 | MAT | S-1 | 0.9 |  | 0.9 | Provisional – calibrate | API 610 material class – base S-5 = 1.00 ¦ بدنه فولاد کربنی، پروانه چدن؛ رینگ چدن؛ شفت فولاد کربنی
MAT¦S-3 | MAT | S-3 | 0.95 |  | 0.95 | Provisional – calibrate | API 610 material class – base S-5 = 1.00 ¦ بدنه فولاد کربنی، پروانه نی‌رزیست (چدن آلیاژی نیکل‌دار)؛ رینگ نی‌رزیست؛ شفت AISI 4140
MAT¦S-4 | MAT | S-4 | 1 |  | 1 | Provisional – calibrate | API 610 material class – base S-5 = 1.00 ¦ بدنه فولاد کربنی، پروانه فولاد کربنی؛ رینگ چدن؛ شفت فولاد کربنی
MAT¦S-5 | MAT | S-5 | 1 |  | 1 | Provisional – calibrate | API 610 material class – base S-5 = 1.00 ¦ بدنه فولاد کربنی، پروانه فولاد کربنی؛ رینگ کروم ۱۲٪ سخت‌شده؛ شفت AISI 4140
MAT¦S-6 | MAT | S-6 | 1.1 |  | 1.1 | Provisional – calibrate | API 610 material class – base S-5 = 1.00 ¦ بدنه فولاد کربنی، پروانه کروم ۱۲٪؛ رینگ کروم ۱۲٪ سخت‌شده؛ شفت کروم ۱۲٪
MAT¦S-8 | MAT | S-8 | 1.25 |  | 1.25 | Provisional – calibrate | API 610 material class – base S-5 = 1.00 ¦ بدنه فولاد کربنی، پروانه فولاد ضدزنگ 316؛ رینگ 316 با روکش سخت؛ شفت 316
MAT¦S-9 | MAT | S-9 | 1.35 |  | 1.35 | Provisional – calibrate | API 610 material class – base S-5 = 1.00 ¦ بدنه فولاد کربنی، پروانه آلیاژ نیکل‌-مس؛ رینگ نیکل‌-مس؛ شفت نیکل‌-مس
MAT¦C-6 | MAT | C-6 | 1.3 |  | 1.3 | Provisional – calibrate | API 610 material class – base S-5 = 1.00 ¦ بدنه کروم ۱۲٪، پروانه کروم ۱۲٪؛ رینگ کروم ۱۲٪ سخت‌شده؛ شفت کروم ۱۲٪
MAT¦A-7 | MAT | A-7 | 1.4 |  | 1.4 | Provisional – calibrate | API 610 material class – base S-5 = 1.00 ¦ بدنه فولاد ضدزنگ آستنیتی، پروانه فولاد ضدزنگ آستنیتی؛ رینگ با روکش سخت؛ شفت آستنیتی
MAT¦A-8 | MAT | A-8 | 1.5 |  | 1.5 | Provisional – calibrate | API 610 material class – base S-5 = 1.00 ¦ بدنه فولاد ضدزنگ 316، پروانه فولاد ضدزنگ 316؛ رینگ با روکش سخت؛ شفت 316
MAT¦D-1 | MAT | D-1 | 1.7 |  | 1.7 | Provisional – calibrate | API 610 material class – base S-5 = 1.00 ¦ بدنه داپلکس، پروانه داپلکس؛ رینگ با روکش سخت؛ شفت داپلکس
MAT¦D-2 | MAT | D-2 | 1.9 |  | 1.9 | Provisional – calibrate | API 610 material class – base S-5 = 1.00 ¦ بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس
MAT¦SS316L (non-API) | MAT | SS316L (non-API) | 1.35 |  | 1.35 | Provisional – calibrate | API 610 material class – base S-5 = 1.00 ¦ بدنه فولاد ضدزنگ 316L، پروانه فولاد ضدزنگ 316L؛ —
MAT¦Not stated | MAT | Not stated | 1 |  | 1 | Provisional – calibrate | API 610 material class – base S-5 = 1.00
SEAL_ARR¦Packing | SEAL_ARR | Packing | 0.9 |  | 0.9 | Provisional – calibrate | Seal type / API 682 arrangement – base Arr 1 = 1.00
SEAL_ARR¦Arr 1 - Single | SEAL_ARR | Arr 1 - Single | 1 |  | 1 | Provisional – calibrate | Seal type / API 682 arrangement – base Arr 1 = 1.00 ¦ Base
SEAL_ARR¦Arr 2 - Dual Unpressurized | SEAL_ARR | Arr 2 - Dual Unpressurized | 1.12 |  | 1.12 | Provisional – calibrate | Seal type / API 682 arrangement – base Arr 1 = 1.00
SEAL_ARR¦Arr 3 - Dual Pressurized | SEAL_ARR | Arr 3 - Dual Pressurized | 1.2 |  | 1.2 | Provisional – calibrate | Seal type / API 682 arrangement – base Arr 1 = 1.00
SEAL_ARR¦Sealless - Magnetic Drive | SEAL_ARR | Sealless - Magnetic Drive | 1.15 |  | 1.15 | Provisional – calibrate | Seal type / API 682 arrangement – base Arr 1 = 1.00
SEAL_ARR¦Sealless - Canned Motor | SEAL_ARR | Sealless - Canned Motor | 1.25 |  | 1.25 | Provisional – calibrate | Seal type / API 682 arrangement – base Arr 1 = 1.00
SEAL_ARR¦Not stated | SEAL_ARR | Not stated | 1 |  | 1 | Provisional – calibrate | Seal type / API 682 arrangement – base Arr 1 = 1.00 ¦ Neutral
SEAL_CAT¦Cat 1 | SEAL_CAT | Cat 1 | 0.95 |  | 0.95 | Provisional – calibrate | API 682 category – base Cat 2 = 1.00
SEAL_CAT¦Cat 2 | SEAL_CAT | Cat 2 | 1 |  | 1 | Provisional – calibrate | API 682 category – base Cat 2 = 1.00 ¦ Base
SEAL_CAT¦Cat 3 | SEAL_CAT | Cat 3 | 1.08 |  | 1.08 | Provisional – calibrate | API 682 category – base Cat 2 = 1.00
SEAL_CAT¦N/A | SEAL_CAT | N/A | 1 |  | 1 | Provisional – calibrate | API 682 category – base Cat 2 = 1.00
SEAL_CAT¦Not stated | SEAL_CAT | Not stated | 1 |  | 1 | Provisional – calibrate | API 682 category – base Cat 2 = 1.00
SEAL_PLAN¦01 | SEAL_PLAN | 01 | 1 |  | 1 | Provisional – calibrate | API 682 seal plan – base Plan 11 = 1.00
SEAL_PLAN¦02 | SEAL_PLAN | 02 | 1 |  | 1 | Provisional – calibrate | API 682 seal plan – base Plan 11 = 1.00
SEAL_PLAN¦11 | SEAL_PLAN | 11 | 1 |  | 1 | Provisional – calibrate | API 682 seal plan – base Plan 11 = 1.00 ¦ Base
SEAL_PLAN¦13 | SEAL_PLAN | 13 | 1 |  | 1 | Provisional – calibrate | API 682 seal plan – base Plan 11 = 1.00
SEAL_PLAN¦14 | SEAL_PLAN | 14 | 1 |  | 1 | Provisional – calibrate | API 682 seal plan – base Plan 11 = 1.00
SEAL_PLAN¦21 | SEAL_PLAN | 21 | 1.01 |  | 1.01 | Provisional – calibrate | API 682 seal plan – base Plan 11 = 1.00
SEAL_PLAN¦23 | SEAL_PLAN | 23 | 1.03 |  | 1.03 | Provisional – calibrate | API 682 seal plan – base Plan 11 = 1.00
SEAL_PLAN¦32 | SEAL_PLAN | 32 | 1.02 |  | 1.02 | Provisional – calibrate | API 682 seal plan – base Plan 11 = 1.00
SEAL_PLAN¦52 | SEAL_PLAN | 52 | 1.04 |  | 1.04 | Provisional – calibrate | API 682 seal plan – base Plan 11 = 1.00
SEAL_PLAN¦53A | SEAL_PLAN | 53A | 1.06 |  | 1.06 | Provisional – calibrate | API 682 seal plan – base Plan 11 = 1.00
SEAL_PLAN¦53B | SEAL_PLAN | 53B | 1.1 |  | 1.1 | Provisional – calibrate | API 682 seal plan – base Plan 11 = 1.00
SEAL_PLAN¦53C | SEAL_PLAN | 53C | 1.1 |  | 1.1 | Provisional – calibrate | API 682 seal plan – base Plan 11 = 1.00
SEAL_PLAN¦54 | SEAL_PLAN | 54 | 1.18 |  | 1.18 | Provisional – calibrate | API 682 seal plan – base Plan 11 = 1.00
SEAL_PLAN¦62 | SEAL_PLAN | 62 | 1.02 |  | 1.02 | Provisional – calibrate | API 682 seal plan – base Plan 11 = 1.00
SEAL_PLAN¦65A | SEAL_PLAN | 65A | 1.01 |  | 1.01 | Provisional – calibrate | API 682 seal plan – base Plan 11 = 1.00
SEAL_PLAN¦72/76 | SEAL_PLAN | 72/76 | 1.04 |  | 1.04 | Provisional – calibrate | API 682 seal plan – base Plan 11 = 1.00
SEAL_PLAN¦11+52 | SEAL_PLAN | 11+52 | 1.04 |  | 1.04 | Provisional – calibrate | API 682 seal plan – base Plan 11 = 1.00
SEAL_PLAN¦11+53B | SEAL_PLAN | 11+53B | 1.1 |  | 1.1 | Provisional – calibrate | API 682 seal plan – base Plan 11 = 1.00
SEAL_PLAN¦23+53B | SEAL_PLAN | 23+53B | 1.12 |  | 1.12 | Provisional – calibrate | API 682 seal plan – base Plan 11 = 1.00
SEAL_PLAN¦N/A | SEAL_PLAN | N/A | 1 |  | 1 | Provisional – calibrate | API 682 seal plan – base Plan 11 = 1.00
SEAL_PLAN¦Not stated | SEAL_PLAN | Not stated | 1 |  | 1 | Provisional – calibrate | API 682 seal plan – base Plan 11 = 1.00 ¦ Neutral
DRV¦Electric Motor | DRV | Electric Motor | 1 |  | 1 | Provisional – calibrate | Driver type – base electric motor = 1.00 ¦ Base
DRV¦Diesel Engine | DRV | Diesel Engine | 1.35 |  | 1.35 | Provisional – calibrate | Driver type – base electric motor = 1.00
DRV¦Steam Turbine | DRV | Steam Turbine | 1.6 |  | 1.6 | Provisional – calibrate | Driver type – base electric motor = 1.00
DRV¦Air / Pneumatic | DRV | Air / Pneumatic | 0.9 |  | 0.9 | Provisional – calibrate | Driver type – base electric motor = 1.00
DRV¦Portable (Air / Electric) | DRV | Portable (Air / Electric) | 1 |  | 1 | Provisional – calibrate | Driver type – base electric motor = 1.00
DRV¦Not stated | DRV | Not stated | 1 |  | 1 | Provisional – calibrate | Driver type – base electric motor = 1.00
NACE¦Y | NACE | Y | 1.05 |  | 1.05 | Provisional – calibrate | NACE MR0175 / ISO 15156 compliance
NACE¦N | NACE | N | 1 |  | 1 | Provisional – calibrate | NACE MR0175 / ISO 15156 compliance ¦ Base
NACE¦Not stated | NACE | Not stated | 1 |  | 1 | Provisional – calibrate | NACE MR0175 / ISO 15156 compliance
SC_DRV¦Y | SC_DRV | Y | 1 |  | 1 | Provisional – calibrate | Scope: driver included (base = Y) ¦ Base
SC_DRV¦N | SC_DRV | N | 0.75 |  | 0.75 | Provisional – calibrate | Scope: driver included (base = Y) ¦ Bare-shaft pump
SC_DRV¦Not stated | SC_DRV | Not stated | 1 |  | 1 | Provisional – calibrate | Scope: driver included (base = Y)
SC_BSP¦Y | SC_BSP | Y | 1 |  | 1 | Provisional – calibrate | Scope: baseplate & coupling (base = Y) ¦ Base
SC_BSP¦N | SC_BSP | N | 0.95 |  | 0.95 | Provisional – calibrate | Scope: baseplate & coupling (base = Y)
SC_BSP¦Not stated | SC_BSP | Not stated | 1 |  | 1 | Provisional – calibrate | Scope: baseplate & coupling (base = Y)
SC_SEAL¦Y | SC_SEAL | Y | 1 |  | 1 | Provisional – calibrate | Scope: seal support system (base = Y) ¦ Base
SC_SEAL¦N | SC_SEAL | N | 0.93 |  | 0.93 | Provisional – calibrate | Scope: seal support system (base = Y)
SC_SEAL¦Not stated | SC_SEAL | Not stated | 1 |  | 1 | Provisional – calibrate | Scope: seal support system (base = Y)
SC_COMM¦Y | SC_COMM | Y | 1 |  | 1 | Provisional – calibrate | Scope: commissioning spares (base = Y) ¦ Base
SC_COMM¦N | SC_COMM | N | 0.98 |  | 0.98 | Provisional – calibrate | Scope: commissioning spares (base = Y)
SC_COMM¦Not stated | SC_COMM | Not stated | 1 |  | 1 | Provisional – calibrate | Scope: commissioning spares (base = Y)
SC_2Y¦Y | SC_2Y | Y | 1.08 |  | 1.08 | Provisional – calibrate | Scope: 2-year spares (base = N)
SC_2Y¦N | SC_2Y | N | 1 |  | 1 | Provisional – calibrate | Scope: 2-year spares (base = N) ¦ Base
SC_2Y¦Not stated | SC_2Y | Not stated | 1 |  | 1 | Provisional – calibrate | Scope: 2-year spares (base = N)
SC_TPI¦Y | SC_TPI | Y | 1.02 |  | 1.02 | Provisional – calibrate | Scope: third-party inspection (base = N)
SC_TPI¦N | SC_TPI | N | 1 |  | 1 | Provisional – calibrate | Scope: third-party inspection (base = N) ¦ Base
SC_TPI¦Not stated | SC_TPI | Not stated | 1 |  | 1 | Provisional – calibrate | Scope: third-party inspection (base = N)
SC_FAT¦Y | SC_FAT | Y | 1.02 |  | 1.02 | Provisional – calibrate | Scope: witnessed FAT (base = N)
SC_FAT¦N | SC_FAT | N | 1 |  | 1 | Provisional – calibrate | Scope: witnessed FAT (base = N) ¦ Base
SC_FAT¦Not stated | SC_FAT | Not stated | 1 |  | 1 | Provisional – calibrate | Scope: witnessed FAT (base = N)
Note on C5: I-1: بدنه چدن، پروانه چدن؛ رینگ چدن؛ شفت فولاد کربنی. کاربرد معمول: آب و سرویس غیرخورنده، دمای پایین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on C6: I-2: بدنه چدن، پروانه برنز؛ رینگ برنز؛ شفت فولاد کربنی. کاربرد معمول: آب، آب آتش‌نشانی و آب شیرین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on C7: S-1: بدنه فولاد کربنی، پروانه چدن؛ رینگ چدن؛ شفت فولاد کربنی. کاربرد معمول: هیدروکربن غیرخورنده. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on C8: S-3: بدنه فولاد کربنی، پروانه نی‌رزیست (چدن آلیاژی نیکل‌دار)؛ رینگ نی‌رزیست؛ شفت AISI 4140. کاربرد معمول: سرویس‌های با سایش یا خوردگی ملایم. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on C9: S-4: بدنه فولاد کربنی، پروانه فولاد کربنی؛ رینگ چدن؛ شفت فولاد کربنی. کاربرد معمول: هیدروکربن عمومی. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on C10: S-5: بدنه فولاد کربنی، پروانه فولاد کربنی؛ رینگ کروم ۱۲٪ سخت‌شده؛ شفت AISI 4140. کاربرد معمول: هیدروکربن عمومی و داغ. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on C11: S-6: بدنه فولاد کربنی، پروانه کروم ۱۲٪؛ رینگ کروم ۱۲٪ سخت‌شده؛ شفت کروم ۱۲٪. کاربرد معمول: هیدروکربن داغ، آب ترش و خوردگی ملایم. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on C12: S-8: بدنه فولاد کربنی، پروانه فولاد ضدزنگ 316؛ رینگ 316 با روکش سخت؛ شفت 316. کاربرد معمول: سرویس‌های خورنده‌تر. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on C13: S-9: بدنه فولاد کربنی، پروانه آلیاژ نیکل‌-مس؛ رینگ نیکل‌-مس؛ شفت نیکل‌-مس. کاربرد معمول: سرویس‌های خاص خورنده. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on C14: C-6: بدنه کروم ۱۲٪، پروانه کروم ۱۲٪؛ رینگ کروم ۱۲٪ سخت‌شده؛ شفت کروم ۱۲٪. کاربرد معمول: آب داغ (تغذیه بویلر) و هیدروکربن داغ. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on C15: A-7: بدنه فولاد ضدزنگ آستنیتی، پروانه فولاد ضدزنگ آستنیتی؛ رینگ با روکش سخت؛ شفت آستنیتی. کاربرد معمول: خوردگی بالا و دمای پایین. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on C16: A-8: بدنه فولاد ضدزنگ 316، پروانه فولاد ضدزنگ 316؛ رینگ با روکش سخت؛ شفت 316. کاربرد معمول: سرویس‌های خورنده. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on C17: D-1: بدنه داپلکس، پروانه داپلکس؛ رینگ با روکش سخت؛ شفت داپلکس. کاربرد معمول: آب شور و آب تولیدی دارای کلراید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on C18: D-2: بدنه سوپرداپلکس، پروانه سوپرداپلکس؛ رینگ با روکش سخت؛ شفت سوپرداپلکس. کاربرد معمول: آب شور و تولیدی با کلراید بالا و خوردگی شدید. (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on C19: SS316L (non-API): بدنه فولاد ضدزنگ 316L، پروانه فولاد ضدزنگ 316L؛ —. کاربرد معمول: ساخت غیر API (مثلاً پمپ بشکه‌ای پرتابل). (خلاصه جدول H.1 استاندارد API 610؛ انتخاب نهایی طبق Annex H/G)
Note on C20: کلاس متریال در منبع ذکر نشده است.
Note on C21: آب‌بندی با گلند پکینگ؛ ارزان‌ترین، با نشتی کنترل‌شده
Note on C22: API 682 Arrangement 1: یک آب‌بند مکانیکی تکی (پایه)
Note on C23: API 682 Arrangement 2: آب‌بند دوبل با سیال Buffer بدون فشار (Plan 52)
Note on C24: API 682 Arrangement 3: آب‌بند دوبل با سیال Barrier تحت فشار (Plan 53A/B/C یا 54)؛ برای سیال سمی یا ترش
Note on C25: پمپ بدون آب‌بند با کوپلینگ مغناطیسی
Note on C26: پمپ بدون آب‌بند با موتور کنسروی (Canned)
Note on C27: ذکر نشده یا کاربرد ندارد؛ ضریب خنثی (۱)
Note on C28: API 682 Category 1: آب‌بند سبک برای پمپ‌های غیر API 610 (ISO)
Note on C29: API 682 Category 2: آب‌بند استاندارد پمپ‌های API 610 (پایه)
Note on C30: API 682 Category 3: سنگین‌ترین، با آزمون تأیید کامل
Note on C31: ذکر نشده یا کاربرد ندارد؛ ضریب خنثی (۱)
Note on C32: ذکر نشده یا کاربرد ندارد؛ ضریب خنثی (۱)
Note on C33: API 682 Plan 01: گردش داخلی از رانش به محفظه آب‌بند
Note on C34: API 682 Plan 02: محفظه بسته بدون گردش
Note on C35: API 682 Plan 11: برگشت از رانش پمپ به آب‌بند (پایه)
Note on C36: API 682 Plan 13: گردش از محفظه آب‌بند به مکش
Note on C37: API 682 Plan 14: ترکیب Plan 11 و 13
Note on C38: API 682 Plan 21: Plan 11 با کولر
Note on C39: API 682 Plan 23: گردش بسته از مسیر کولر (سیال داغ)
Note on C40: API 682 Plan 32: تزریق سیال تمیز از منبع خارجی
Note on C41: API 682 Plan 52: سیال Buffer بدون فشار برای آب‌بند دوبل (Arr 2)
Note on C42: API 682 Plan 53A: Barrier تحت فشار با مخزن و گاز نیتروژن (Arr 3)
Note on C43: API 682 Plan 53B: Barrier تحت فشار با Bladder Accumulator (Arr 3)
Note on C44: API 682 Plan 53C: Barrier تحت فشار با پیستون Accumulator (Arr 3)
Note on C45: API 682 Plan 54: سیستم Barrier خارجی کامل تحت فشار
Note on C46: API 682 Plan 62: Quench با بخار یا آب در سمت اتمسفر
Note on C47: API 682 Plan 65A: تخلیه و هشدار نشتی
Note on C48: API 682 Plan 72/76: آب‌بند گازی (Buffer یا تخلیه بخارات)
Note on C49: API 682 Plan 11+52: Plan 11 روی آب‌بند داخلی + Plan 52
Note on C50: API 682 Plan 11+53B: Plan 11 + Plan 53B
Note on C51: API 682 Plan 23+53B: Plan 23 + Plan 53B
Note on C52: API 682 Plan N/A: کاربرد ندارد یا ذکر نشده
Note on C53: API 682 Plan Not stated: کاربرد ندارد یا ذکر نشده
Note on C54: موتور برقی (پایه)
Note on C55: موتور دیزلی (مثلاً پمپ آتش‌نشانی دیزلی)
Note on C56: توربین بخار
Note on C57: محرک بادی
Note on C58: محرک پرتابل بادی یا برقی (پمپ بشکه‌ای)
Note on C59: ذکر نشده یا کاربرد ندارد؛ ضریب خنثی (۱)
Note on C60: الزام NACE MR0175 / ISO 15156 برای سرویس ترش (H2S)
Note on C61: بدون الزام NACE (پایه)
Note on C62: ذکر نشده یا کاربرد ندارد؛ ضریب خنثی (۱)
Note on C63: محرک (موتور) جزو قیمت: بله
Note on C64: محرک (موتور) جزو قیمت: خیر
Note on C65: محرک (موتور) جزو قیمت: در منبع ذکر نشده (ضریب ۱)
Note on C66: شاسی و کوپلینگ جزو قیمت: بله
Note on C67: شاسی و کوپلینگ جزو قیمت: خیر
Note on C68: شاسی و کوپلینگ جزو قیمت: در منبع ذکر نشده (ضریب ۱)
Note on C69: سیستم جانبی آب‌بند (مخزن، Accumulator، کولر) جزو قیمت: بله
Note on C70: سیستم جانبی آب‌بند (مخزن، Accumulator، کولر) جزو قیمت: خیر
Note on C71: سیستم جانبی آب‌بند (مخزن، Accumulator، کولر) جزو قیمت: در منبع ذکر نشده (ضریب ۱)
Note on C72: یدکی راه‌اندازی جزو قیمت: بله
Note on C73: یدکی راه‌اندازی جزو قیمت: خیر
Note on C74: یدکی راه‌اندازی جزو قیمت: در منبع ذکر نشده (ضریب ۱)
Note on C75: یدکی دو سال بهره‌برداری جزو قیمت: بله
Note on C76: یدکی دو سال بهره‌برداری جزو قیمت: خیر
Note on C77: یدکی دو سال بهره‌برداری جزو قیمت: در منبع ذکر نشده (ضریب ۱)
Note on C78: هزینه بازرسی شخص ثالث جزو قیمت: بله
Note on C79: هزینه بازرسی شخص ثالث جزو قیمت: خیر
Note on C80: هزینه بازرسی شخص ثالث جزو قیمت: در منبع ذکر نشده (ضریب ۱)
Note on C81: آزمون عملکرد کارخانه با حضور کارفرما جزو قیمت: بله
Note on C82: آزمون عملکرد کارخانه با حضور کارفرما جزو قیمت: خیر
Note on C83: آزمون عملکرد کارخانه با حضور کارفرما جزو قیمت: در منبع ذکر نشده (ضریب ۱)

## Lookup_Codes
LOOKUP CODES – منبع همه Dropdownها
برای افزودن گزینه، مقدار را به انتهای ستون اضافه کنید (محدوده تا ردیف 60). گزینه‌های دارای ضریب باید در Factors_ROT هم اضافه شوند.
SubCat | Service | Std | IPS | Family | API610 | Power_Basis | YN | YNS | Currency | Year | Incoterm | Phase | Origin | AVL | Rank | TBE | MAT | SEAL_ARR | SEAL_CAT | SEAL_PLAN | DRV | SRCH_Project | SRCH_SubCat | SRCH_Service | SRCH_Std | SRCH_Family | SRCH_API610 | SRCH_MAT | SRCH_YNS | SRCH_SEAL_ARR | SRCH_DRV | SRCH_Year | SRCH_YN
ROT-CRU | Crude Oil | API 610 | IPS-G-PM-105 | Centrifugal | OH1 | Motor Rated | Y | Y | EUR | 1385 | EXW | Conceptual | Domestic | NIOC/NISOC Approved | Rank 1 | Y | I-1 | Packing | Cat 1 | 01 | Electric Motor | (All) | (All) | (All) | (All) | (All) | (All) | (All) | (All) | (All) | (All) | (All) | (All)
ROT-WAT | Slop / Dirty Oil | API 674 | IPS-M-PM-115 | Centrifugal - Submersible | OH2 | Shaft (Absorbed) | N | N | USD | 1386 | FCA | Basic Design | Import | Conditional | Rank 2 | N | I-2 | Arr 1 - Single | Cat 2 | 02 | Diesel Engine | (نام پروژه در فایل قید نشده است) – CSV 18061405 | ROT-CRU | Crude Oil | API 610 | Centrifugal | OH1 | I-1 | Y | Packing | Electric Motor | 1393 | Y
ROT-INJ | Produced / Disposal Water | API 675 | IPS-M-PM-125 | PD-Rotary (Gear) | OH3 | Not stated |  | Not stated | IRR | 1387 | FOB | FEED | Domestic (Licensed) | Non-AVL | Rank 3 | Pending | S-1 | Arr 2 - Dual Unpressurized | Cat 3 | 11 | Steam Turbine | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | ROT-WAT | Slop / Dirty Oil | API 674 | Centrifugal - Submersible | OH2 | I-2 | N | Arr 1 - Single | Diesel Engine | 1402 | N
ROT-DRN | Process / Dilution Water | API 676 | IPS-M-PM-140 | PD-Rotary (Progressing Cavity) | OH4 |  |  |  |  | 1388 | CFR | Detail Engineering |  | Not checked |  |  | S-3 | Arr 3 - Dual Pressurized | N/A | 13 | Air / Pneumatic | Gachsaran 4 | ROT-INJ | Produced / Disposal Water | API 675 | PD-Rotary (Gear) | OH3 | S-1 | Not stated | Arr 2 - Dual Unpressurized | Steam Turbine | 1404
ROT-AUX | Deaerated Water | ISO 13709 | None | PD-Rotary (Screw) | OH5 |  |  |  |  | 1389 | CIF | Tender / Procurement |  |  |  |  | S-4 | Sealless - Magnetic Drive | Not stated | 14 | Portable (Air / Electric) | Koopal Asmari | ROT-DRN | Process / Dilution Water | API 676 | PD-Rotary (Progressing Cavity) | OH4 | S-3 |  | Arr 3 - Dual Pressurized | Air / Pneumatic | (Not stated)
ROT-FIR | Fresh / Potable Water | ISO 5199 |  | PD-Rotary (Sliding Vane) | OH6 |  |  |  |  | 1390 | DAP | EPC Contract |  |  |  |  | S-5 | Sealless - Canned Motor |  | 21 | Not stated | Koopal Bangestan | ROT-AUX | Deaerated Water | ISO 13709 | PD-Rotary (Screw) | OH5 | S-4 |  | Sealless - Magnetic Drive | Portable (Air / Electric)
| Oily Water / Drain | ISO 2858 |  | PD-Reciprocating (Plunger) | BB1 |  |  |  |  | 1391 | DDP | Not stated |  |  |  |  | S-6 | Not stated |  | 23 |  | Pazanan 2 | ROT-FIR | Fresh / Potable Water | ISO 5199 | PD-Rotary (Sliding Vane) | OH6 | S-5 |  | Sealless - Canned Motor | Not stated
| Sludge | NFPA 20 |  | Metering (Diaphragm) | BB2 |  |  |  |  | 1392 | Domestic Delivered (IRR) | [5 empty] | S-8 |  |  | 32 |  |  |  | Oily Water / Drain | ISO 2858 | PD-Reciprocating (Plunger) | BB1 | S-6 |  | Not stated
| Chemical | JIS B 8325 |  | Metering (Plunger) | BB3 |  |  |  |  | 1393 | Not stated | [5 empty] | S-9 |  |  | 52 |  |  |  | Sludge | NFPA 20 | Metering (Diaphragm) | BB2 | S-8
| Diesel / Fuel Oil | Manufacturer Std |  | Portable Barrel | BB4 |  |  |  |  | 1394 | [6 empty] | C-6 |  |  | 53A |  |  |  | Chemical | JIS B 8325 | Metering (Plunger) | BB3 | S-9
| Fire Water | Not stated |  | Jet / Eductor | BB5 |  |  |  |  | 1395 | [6 empty] | A-7 |  |  | 53B |  |  |  | Diesel / Fuel Oil | Manufacturer Std | Portable Barrel | BB4 | C-6
| Cooling / Seal Water |  |  | Not stated | VS1 |  |  |  |  | 1396 | [6 empty] | A-8 |  |  | 53C |  |  |  | Fire Water | Not stated | Jet / Eductor | BB5 | A-7
| Other |  |  |  | VS2 |  |  |  |  | 1397 | [6 empty] | D-1 |  |  | 54 |  |  |  | Cooling / Seal Water |  | Not stated | VS1 | A-8
[5 empty] | VS3 |  |  |  |  | 1398 | [6 empty] | D-2 |  |  | 62 |  |  |  | Other |  |  | VS2 | D-1
[5 empty] | VS4 |  |  |  |  | 1399 | [6 empty] | SS316L (non-API) |  |  | 65A | [6 empty] | VS3 | D-2
[5 empty] | VS5 |  |  |  |  | 1400 | [6 empty] | Not stated |  |  | 72/76 | [6 empty] | VS4 | SS316L (non-API)
[5 empty] | VS6 |  |  |  |  | 1401 | [9 empty] | 11+52 | [6 empty] | VS5 | Not stated
[5 empty] | VS7 |  |  |  |  | 1402 | [9 empty] | 11+53B | [6 empty] | VS6
[5 empty] | OH (unspecified) |  |  |  |  | 1403 | [9 empty] | 23+53B | [6 empty] | VS7
[5 empty] | BB (unspecified) |  |  |  |  | 1404 | [9 empty] | N/A | [6 empty] | OH (unspecified)
[5 empty] | VS (unspecified) |  |  |  |  | 1405 | [9 empty] | Not stated | [6 empty] | BB (unspecified)
[5 empty] | N/A (non-API 610) |  |  |  |  | (Not stated) | [16 empty] | VS (unspecified)
[5 empty] | Not stated | [21 empty] | N/A (non-API 610)
Not stated

## Escalation_Index
ESCALATION_INDEX – شاخص قیمت تولیدکننده پمپ (Eurostat sts_inppd_a, NACE C28.13, EA20)
Source: Pump_Escalation_Validation.xlsx, sheet Indices, Table 3 (C51:C71) = Jalali-year blend of Eurostat sts_inppd_a, NACE C28.13, EA20 (2021=100): PPI(Jalali Y) = 0.79×PPI(Y+621) + 0.21×PPI(Y+622) (Indices C3). CPI is not used.
Jalali Year | PPI C28.13 EA20 (2021=100), Jalali-year blend | Gregorian ref. | Source / status
1385 | 77.193 | 2006 (79%) / 2007 (21%) | Eurostat sts_inppd_a (imputed before 2018) ¦ Pump_Escalation_Validation.xlsx Indices C51
1386 | 80.157 | 2007 (79%) / 2008 (21%) | Eurostat sts_inppd_a (imputed before 2018) ¦ Pump_Escalation_Validation.xlsx Indices C52
1387 | 81.962 | 2008 (79%) / 2009 (21%) | Eurostat sts_inppd_a (imputed before 2018) ¦ Pump_Escalation_Validation.xlsx Indices C53
1388 | 83.847 | 2009 (79%) / 2010 (21%) | Eurostat sts_inppd_a (imputed before 2018) ¦ Pump_Escalation_Validation.xlsx Indices C54
1389 | 84.778 | 2010 (79%) / 2011 (21%) | Eurostat sts_inppd_a (imputed before 2018) ¦ Pump_Escalation_Validation.xlsx Indices C55
1390 | 86.662 | 2011 (79%) / 2012 (21%) | Eurostat sts_inppd_a (imputed before 2018) ¦ Pump_Escalation_Validation.xlsx Indices C56
1391 | 88.715 | 2012 (79%) / 2013 (21%) | Eurostat sts_inppd_a (imputed before 2018) ¦ Pump_Escalation_Validation.xlsx Indices C57
1392 | 90.173 | 2013 (79%) / 2014 (21%) | Eurostat sts_inppd_a (imputed before 2018) ¦ Pump_Escalation_Validation.xlsx Indices C58
1393 | 91.347 | 2014 (79%) / 2015 (21%) | Eurostat sts_inppd_a (imputed before 2018) ¦ Pump_Escalation_Validation.xlsx Indices C59
1394 | 92.047 | 2015 (79%) / 2016 (21%) | Eurostat sts_inppd_a (imputed before 2018) ¦ Pump_Escalation_Validation.xlsx Indices C60
1395 | 92.81 | 2016 (79%) / 2017 (21%) | Eurostat sts_inppd_a (imputed before 2018) ¦ Pump_Escalation_Validation.xlsx Indices C61
1396 | 93.81 | 2017 (79%) / 2018 (21%) | Eurostat sts_inppd_a (imputed before 2018) ¦ Pump_Escalation_Validation.xlsx Indices C62
1397 | 94.978 | 2018 (79%) / 2019 (21%) | Eurostat sts_inppd_a ¦ Pump_Escalation_Validation.xlsx Indices C63
1398 | 96.694 | 2019 (79%) / 2020 (21%) | Eurostat sts_inppd_a ¦ Pump_Escalation_Validation.xlsx Indices C64
1399 | 98.262 | 2020 (79%) / 2021 (21%) | Eurostat sts_inppd_a ¦ Pump_Escalation_Validation.xlsx Indices C65
1400 | 101.953 | 2021 (79%) / 2022 (21%) | Eurostat sts_inppd_a ¦ Pump_Escalation_Validation.xlsx Indices C66
1401 | 111.253 | 2022 (79%) / 2023 (21%) | Eurostat sts_inppd_a ¦ Pump_Escalation_Validation.xlsx Indices C67
1402 | 119.251 | 2023 (79%) / 2024 (21%) | Eurostat sts_inppd_a ¦ Pump_Escalation_Validation.xlsx Indices C68
1403 | 121.952 | 2024 (79%) / 2025 (21%) | Eurostat sts_inppd_a ¦ Pump_Escalation_Validation.xlsx Indices C69
1404 | 123.416 | 2025 (79%) / 2026 (21%) | Eurostat 2025 (79%) + 2026 forecast (21%) ¦ Pump_Escalation_Validation.xlsx Indices C70
1405 | 125.885 | 2026 (79%) / 2027 (21%) | FORECAST – 2026 not yet published; +2%/yr trend (Indices C4); 21% weight of 2027 also forecast ¦ Pump_Escalation_Validation.xlsx Indices C71

## Assumptions & FX Reference
ASSUMPTIONS & FX REFERENCE – نرخ تسعیر و پارامترهای تعدیل
جدول FX از Pumps_Price_Bank_Final_Updated_v2 منتقل شده است (فقط سال‌های دارای مرجع در ستون E تأییدشده‌اند). پارامترهای زرد ورودی کاربر هستند.
Jalali Year | USD → IRR | EUR → IRR | EUR / USD Ratio | Basis / Document Reference Source | Parameter | Value | Note
1385 | 9148 | 11285 | 1.2336 | (not found in the source files – add if needed) | Target Year (سال هدف تعدیل) | 1404 | Dropdown. سال ۱۴۰۵ در Escalation_Index پیش‌بینی است.
1386 | 9202 | 11781 | 1.2803 | (not found in the source files – add if needed) | Target EUR→IRR (auto) | 695268 | از جدول FX
1387 | 9300 | 14260 | 1.5333 | (not found in the source files – add if needed) | Target EUR→IRR override (optional) |  | نرخ روز را در صورت نیاز وارد کنید
1388 | 9900 | 13400 | 1.3535 | (not found in the source files – add if needed) | Target EUR→IRR used | 695268
1389 | 10200 | 13800 | 1.3529 | (not found in the source files – add if needed) | Target USD→IRR (auto) | 658533 | از جدول FX
1390 | 11300 | 15750 | 1.3938 | (not found in the source files – add if needed) | Target USD→IRR override (optional) |  | نرخ روز را در صورت نیاز وارد کنید
1391 | 19000 | 25500 | 1.3421 | (not found in the source files – add if needed) | Target USD→IRR used | 658533
1392 | 36300 | 42000 | 1.157 | EUR: free-market euro rate 42,000 (label 'نرخ آزاد یورو', Maroon3 sheets p.lab.1392 / SEFTY.p.1392). | PPI target year (C28.13 EA20) | 123.416
1393 | 31000 | 40530.8 | 1.3074 | EUR: 40,530.8 – Maroon3 sheet Inflation, label 'نرخ تسعیر ارز سال 93' (currency not written in the label; presumed EUR – verify). | Price floor, EUR (API 610 centrifugal, class S/D) | 25000 | روش تأییدشده تعدیل پمپ (مهر ۱۴۰۵)
1394 | 33550 | 36750 | 1.0954 | (not found in the source files – add if needed) | Floor base year | 1404
1395 | 34600 | 38800 | 1.1214 | (not found in the source files – add if needed) | PPI of floor base year | 123.416
1396 | 37300 | 40250 | 1.0791 | (not found in the source files – add if needed) | Cost-capacity exponent n (price ∝ kW^n) | 0.6 | Provisional – calibrate
1397 | 47700 | 59000 | 1.2369 | (not found in the source files – add if needed) | Pump efficiency for estimated kW | 0.6 | kW ≈ Q[m³/h]·H[m] / (367·η)؛ آب با SG=1 فرض شده
1398 | 135000 | 152800 | 1.1319 | (not found in the source files – add if needed)
1399 | 161000 | 172200 | 1.0696 | (not found in the source files – add if needed)
1400 | 252000 | 298400 | 1.1841 | (not found in the source files – add if needed)
1401 | 263000 | 289500 | 1.1008 | (not found in the source files – add if needed)
1402 | 420000 | 529500 | 1.2607 | USD: 420,000 – Gachsaran4 sheet Procurement 'ارز مرجع' (PEP Rev. 1402/05).
1403 | 600500 | 653000 | 1.0874 | (not found in the source files – add if needed)
1404 | 658533 | 695268 | 1.0558 | USD: 658,533 = cached external-link value used by Pazanan2 formulas (assumed IRR per USD; verify). EUR = USD x 1.0558 (cached ratio) – derived.
1405 | 1818181.8182 | 2000000 | 1.1 | EUR: 2,000,000 – Maroon3 sheet Inflation, label 'یورو به ریال' (1405 estimate). USD = EUR / 1.1 (same sheet) – derived. ¦ اصلاح: فرمول دوری B25↔D25 حذف و USD = EUR/1.1 مستقیم شد.

## Verification_Log
VERIFICATION LOG – صحت‌سنجی فیلدبه‌فیلد با فایل‌های مرجع
هر ردیف یک فیلد از یک رکورد است که مستقیماً با سلول فایل مرجع مقایسه شده (نه با بانک قدیم). مراجع: KPL-476 R03، PEP-Rev.140205 گچساران، PC-ME 14040105 پازنان ۲، 18061405_Pump_only_CSV.csv، نمونه قیمتی نمک‌زدایی.
Result | Count | معنی
Match | 1281 | مطابق مرجع
Inferred – marked | 199 | در مرجع نیست؛ استنباطی و زرد شده (دلیل در Note سلول)
Derived – marked | 7 | محاسبه‌شده از داده مرجع (مثلاً هد از اختلاف فشار)؛ زرد شده
Match (INS-PUMP sheet name) | 5 | نام مطابق شیت INS-PUMP همان گزارش (دقیق‌تر از شیت PUMPS)
Total checks | 1492
Row | Project | Tag No. | Field | Bank value | Source value | Source reference | Result
1 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Equipment Name | 2nd Stage Separators Oil Pumps | 2nd Stage Separators Oil Pumps | CSV line 5 col C | Match
1 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Pump Family | Centrifugal | Centrifugal | CSV line 5 col E | Match
1 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Diff. Head (m) | 95.8 | 95.8 | CSV line 5 col G | Match
1 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Power (kW) | 54.3 | 54.3 | CSV line 5 col H | Match
1 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Driver Type | Electric Motor | Electric Motor | CSV line 5 col F | Match
1 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Currency | USD | USD | CSV line 5 col I | Match
1 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Unit Price | 240000 | 240000 | CSV line 5 col I | Match
2 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Equipment Name | 3rd Stage Separators Oil Pumps | 3rd Stage Separators Oil Pumps | CSV line 6 col C | Match
2 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Pump Family | Centrifugal | Centrifugal | CSV line 6 col E | Match
2 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Diff. Head (m) | 59.9 | 59.9 | CSV line 6 col G | Match
2 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Power (kW) | 33.1 | 33.1 | CSV line 6 col H | Match
2 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Driver Type | Electric Motor | Electric Motor | CSV line 6 col F | Match
2 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Currency | USD | USD | CSV line 6 col I | Match
2 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Unit Price | 280000 | 280000 | CSV line 6 col I | Match
3 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Equipment Name | Stabilized Oil Pump | Stabilized Oil Pump | CSV line 7 col C | Match
3 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Pump Family | Centrifugal | Centrifugal | CSV line 7 col E | Match
3 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Diff. Head (m) | 34.8 | 34.8 | CSV line 7 col G | Match
3 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Power (kW) | 57.4 | 57.4 | CSV line 7 col H | Match
3 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Driver Type | Electric Motor | Electric Motor | CSV line 7 col F | Match
3 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Currency | USD | USD | CSV line 7 col I | Match
3 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Unit Price | 250000 | 250000 | CSV line 7 col I | Match
4 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Equipment Name | Product Oil Pump | Product Oil Pump | CSV line 8 col C | Match
4 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Pump Family | Centrifugal | Centrifugal | CSV line 8 col E | Match
4 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Diff. Head (m) | 329 | 329 | CSV line 8 col G | Match
4 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Power (kW) | 379 | 379 | CSV line 8 col H | Match
4 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Driver Type | Electric Motor | Electric Motor | CSV line 8 col F | Match
4 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Currency | USD | USD | CSV line 8 col I | Match
4 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Unit Price | 420000 | 420000 | CSV line 8 col I | Match
5 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Equipment Name | Off Spec Crude Pump | Off Spec Crude Pump | CSV line 9 col C | Match
5 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Pump Family | Centrifugal | Centrifugal | CSV line 9 col E | Match
5 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Diff. Head (m) | 311.3 | 311.3 | CSV line 9 col G | Match
5 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Power (kW) | 48 | 48 | CSV line 9 col H | Match
5 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Driver Type | Electric Motor | Electric Motor | CSV line 9 col F | Match
5 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Currency | USD | USD | CSV line 9 col I | Match
5 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Unit Price | 75000 | 75000 | CSV line 9 col I | Match
6 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Equipment Name | Second Stage Desalter Water Criculated Pump | Second Stage Desalter Water Criculated Pump | CSV line 10 col C | Match
6 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Pump Family | Centrifugal | Centrifugal | CSV line 10 col E | Match
6 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Diff. Head (m) | 32 | 32 | CSV line 10 col G | Match
6 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Power (kW) | 2.2 | 2.2 | CSV line 10 col H | Match
6 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Driver Type | Electric Motor | Electric Motor | CSV line 10 col F | Match
6 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Currency | USD | USD | CSV line 10 col I | Match
6 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Unit Price | 60000 | 60000 | CSV line 10 col I | Match
7 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Equipment Name | Degassing Water Pump | Degassing Water Pump | CSV line 11 col C | Match
7 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Pump Family | Centrifugal | Centrifugal | CSV line 11 col E | Match
7 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Diff. Head (m) | 36.2 | 36.2 | CSV line 11 col G | Match
7 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Power (kW) | 13.1 | 13.1 | CSV line 11 col H | Match
7 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Driver Type | Electric Motor | Electric Motor | CSV line 11 col F | Match
7 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Currency | USD | USD | CSV line 11 col I | Match
7 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Unit Price | 60000 | 60000 | CSV line 11 col I | Match
8 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Equipment Name | Disposal Water Pump | Disposal Water Pump | CSV line 12 col C | Match
8 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Pump Family | Centrifugal | Centrifugal | CSV line 12 col E | Match
8 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Diff. Head (m) | 1383 | 1383 | CSV line 12 col G | Match
8 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Power (kW) | 423 | 423 | CSV line 12 col H | Match
8 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Driver Type | Electric Motor | Electric Motor | CSV line 12 col F | Match
8 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Currency | USD | USD | CSV line 12 col I | Match
8 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Unit Price | 410000 | 410000 | CSV line 12 col I | Match
9 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Equipment Name | Fresh Water Pump | Fresh Water Pump | CSV line 13 col C | Match
9 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Pump Family | Centrifugal | Centrifugal | CSV line 13 col E | Match
9 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Diff. Head (m) | 41 | 41 | CSV line 13 col G | Match
9 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Power (kW) | 3.9 | 3.9 | CSV line 13 col H | Match
9 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Driver Type | Electric Motor | Electric Motor | CSV line 13 col F | Match
9 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Currency | USD | USD | CSV line 13 col I | Match
9 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Unit Price | 8000 | 8000 | CSV line 13 col I | Match
10 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Equipment Name | Closed Drain Pump | Closed Drain Pump | CSV line 14 col C | Match
10 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Pump Family | Centrifugal | Centrifugal | CSV line 14 col E | Match
10 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Diff. Head (m) | 120 | 120 | CSV line 14 col G | Match
10 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Power (kW) | 13.7 | 13.7 | CSV line 14 col H | Match
10 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Driver Type | Electric Motor | Electric Motor | CSV line 14 col F | Match
10 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Currency | USD | USD | CSV line 14 col I | Match
10 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Unit Price | 40000 | 40000 | CSV line 14 col I | Match
11 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Equipment Name | Diesel Unlodaing pump | Diesel Unlodaing pump | CSV line 15 col C | Match
11 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Pump Family | PD-Rotary (Sliding Vane) | Sliding valve | CSV line 15 col E | Match
11 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Diff. Head (m) | 27.2 | 27.2 | CSV line 15 col G | Match
11 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Power (kW) | 4 | 4 | CSV line 15 col H | Match
11 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Driver Type | Electric Motor | Electric Motor | CSV line 15 col F | Match
11 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Currency | USD | USD | CSV line 15 col I | Match
11 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Unit Price | 5000 | 5000 | CSV line 15 col I | Match
12 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Equipment Name | Diesel Transfer pump | Diesel Transfer pump | CSV line 16 col C | Match
12 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Pump Family | PD-Rotary (Screw) | Screw | CSV line 16 col E | Match
12 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Diff. Head (m) | 40.8 | 40.8 | CSV line 16 col G | Match
12 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Power (kW) | 0.8 | 0.8 | CSV line 16 col H | Match
12 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Driver Type | Electric Motor | Electric Motor | CSV line 16 col F | Match
12 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Currency | USD | USD | CSV line 16 col I | Match
12 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Unit Price | 3000 | 3000 | CSV line 16 col I | Match
13 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Equipment Name | Sludge Discharge Water Jet Pump | Sludge Discharge Water Jet Pump | CSV line 17 col C | Match
13 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Pump Family | Centrifugal | Centrifugal | CSV line 17 col E | Match
13 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Diff. Head (m) | 15 | 15 | CSV line 17 col G | Match
13 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Power (kW) | 5 | 5 | CSV line 17 col H | Match
13 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Driver Type | Electric Motor | Electric Motor | CSV line 17 col F | Match
13 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Currency | USD | USD | CSV line 17 col I | Match
13 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Unit Price | 3000 | 3000 | CSV line 17 col I | Match
14 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Equipment Name | Flare KO Drum Pumps | Flare KO Drum Pumps | CSV line 18 col C | Match
14 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Pump Family | Centrifugal | Centrifugal | CSV line 18 col E | Match
14 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Diff. Head (m) | 18 | 18 | CSV line 18 col G | Match
14 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Power (kW) | 2 | 2 | CSV line 18 col H | Match
14 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Driver Type | Electric Motor | Electric Motor | CSV line 18 col F | Match
14 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Currency | USD | USD | CSV line 18 col I | Match
14 | (نام پروژه در فایل قید نشده است) – CSV 18061405 | (Not stated in source document) | Unit Price | 40000 | 40000 | CSV line 18 col I | Match
15 | Gachsaran 4 | P-001-A/B | Equipment Name | MAIN TRANSFER PUMPS | MAIN TRANSFER PUMPS | P.ME!D11 | Match
15 | Gachsaran 4 | P-001-A/B | Quantity | 2 | 2 | P.ME!G11 | Match
15 | Gachsaran 4 | P-001-A/B | Pump Family | Centrifugal | (not stated) |  | Inferred – marked
15 | Gachsaran 4 | P-001-A/B | Capacity (m³/h) | 500 | 500 | P.ME!E11 | Match
15 | Gachsaran 4 | P-001-A/B | Discharge Pressure (barg) | 15.2 | 15.2 | P.ME!E11 | Match
15 | Gachsaran 4 | P-001-A/B | Power (kW) | 216.3 | 216.3 | P.ME!E11 | Match
15 | Gachsaran 4 | P-001-A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
15 | Gachsaran 4 | P-001-A/B | Currency | EUR | EUR | P.ME!H11 | Match
15 | Gachsaran 4 | P-001-A/B | Unit Price | 385000 | 385000 | P.ME!H11 | Match
16 | Gachsaran 4 | P-002-A/B | Equipment Name | AUXILLIARY TRANSFER PUMPS | AUXILLIARY TRANSFER PUMPS | P.ME!D12 | Match
16 | Gachsaran 4 | P-002-A/B | Quantity | 2 | 2 | P.ME!G12 | Match
16 | Gachsaran 4 | P-002-A/B | Pump Family | Centrifugal | (not stated) |  | Inferred – marked
16 | Gachsaran 4 | P-002-A/B | Capacity (m³/h) | 250 | 250 | P.ME!E12 | Match
16 | Gachsaran 4 | P-002-A/B | Discharge Pressure (barg) | 15.2 | 15.2 | P.ME!E12 | Match
16 | Gachsaran 4 | P-002-A/B | Power (kW) | 108.1 | 108.1 | P.ME!E12 | Match
16 | Gachsaran 4 | P-002-A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
16 | Gachsaran 4 | P-002-A/B | Currency | EUR | EUR | P.ME!H12 | Match
16 | Gachsaran 4 | P-002-A/B | Unit Price | 135000 | 135000 | P.ME!H12 | Match
17 | Gachsaran 4 | P-003-A/B | Equipment Name | OFF-SPEC PUMPS | OFF-SPEC PUMPS | P.ME!D13 | Match
17 | Gachsaran 4 | P-003-A/B | Quantity | 2 | 2 | P.ME!G13 | Match
17 | Gachsaran 4 | P-003-A/B | Pump Family | Centrifugal | (not stated) |  | Inferred – marked
17 | Gachsaran 4 | P-003-A/B | Capacity (m³/h) | 100 | 100 | P.ME!E13 | Match
17 | Gachsaran 4 | P-003-A/B | Discharge Pressure (barg) | 15.5 | 15.5 | P.ME!E13 | Match
17 | Gachsaran 4 | P-003-A/B | Power (kW) | 44.2 | 44.2 | P.ME!E13 | Match
17 | Gachsaran 4 | P-003-A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
17 | Gachsaran 4 | P-003-A/B | Currency | EUR | EUR | P.ME!H13 | Match
17 | Gachsaran 4 | P-003-A/B | Unit Price | 140000 | 140000 | P.ME!H13 | Match
18 | Gachsaran 4 | P-005-A/B | Equipment Name | DEGASSING WATER PUMPS | DEGASSING WATER PUMPS | P.ME!D14 | Match
18 | Gachsaran 4 | P-005-A/B | Quantity | 2 | 2 | P.ME!G14 | Match
18 | Gachsaran 4 | P-005-A/B | Pump Family | Centrifugal | (not stated) |  | Inferred – marked
18 | Gachsaran 4 | P-005-A/B | Capacity (m³/h) | 30 | 30 | P.ME!E14 | Match
18 | Gachsaran 4 | P-005-A/B | Discharge Pressure (barg) | 3 | 3 | P.ME!E14 | Match
18 | Gachsaran 4 | P-005-A/B | Power (kW) | 2.7 | 2.7 | P.ME!E14 | Match
18 | Gachsaran 4 | P-005-A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
18 | Gachsaran 4 | P-005-A/B | Currency | EUR | EUR | P.ME!H14 | Match
18 | Gachsaran 4 | P-005-A/B | Unit Price | 34000 | 34000 | P.ME!H14 | Match
19 | Gachsaran 4 | P-103 | Equipment Name | DILUTION WATER PUMPS | DILUTION WATER PUMPS | P.ME!D17 | Match
19 | Gachsaran 4 | P-103 | Quantity | 1 | 1 | P.ME!G17 | Match
19 | Gachsaran 4 | P-103 | Pump Family | Centrifugal | (not stated) |  | Inferred – marked
19 | Gachsaran 4 | P-103 | Capacity (m³/h) | 40 | 40 | P.ME!E17 | Match
19 | Gachsaran 4 | P-103 | Discharge Pressure (barg) | 10.4 | 10.4 | P.ME!E17 | Match
19 | Gachsaran 4 | P-103 | Power (kW) | 12 | 12 | P.ME!E17 | Match
19 | Gachsaran 4 | P-103 | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
19 | Gachsaran 4 | P-103 | Currency | EUR | EUR | P.ME!H17 | Match
19 | Gachsaran 4 | P-103 | Unit Price | 29000 | 29000 | P.ME!H17 | Match
20 | Gachsaran 4 | P-106-A1/A2 | Equipment Name | DILUTION WATER PUMPS | DILUTION WATER PUMPS | P.ME!D18 | Match
20 | Gachsaran 4 | P-106-A1/A2 | Quantity | 2 | 2 | P.ME!G18 | Match
20 | Gachsaran 4 | P-106-A1/A2 | Pump Family | Centrifugal | (not stated) |  | Inferred – marked
20 | Gachsaran 4 | P-106-A1/A2 | Capacity (m³/h) | 20 | 20 | P.ME!E18 | Match
20 | Gachsaran 4 | P-106-A1/A2 | Discharge Pressure (barg) | 10.4 | 10.4 | P.ME!E18 | Match
20 | Gachsaran 4 | P-106-A1/A2 | Power (kW) | 6 | 6 | P.ME!E18 | Match
20 | Gachsaran 4 | P-106-A1/A2 | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
20 | Gachsaran 4 | P-106-A1/A2 | Currency | EUR | EUR | P.ME!H18 | Match
20 | Gachsaran 4 | P-106-A1/A2 | Unit Price | 27500 | 27500 | P.ME!H18 | Match
21 | Gachsaran 4 | P-102-A/B | Equipment Name | DEAERATED WATER PUMPS | DEAERATED WATER PUMPS | P.ME!D20 | Match
21 | Gachsaran 4 | P-102-A/B | Quantity | 2 | 2 | P.ME!G20 | Match
21 | Gachsaran 4 | P-102-A/B | Pump Family | Centrifugal | (not stated) |  | Inferred – marked
21 | Gachsaran 4 | P-102-A/B | Capacity (m³/h) | 20 | 20 | P.ME!E20 | Match
21 | Gachsaran 4 | P-102-A/B | Discharge Pressure (barg) | 2.4 | 2.4 | P.ME!E20 | Match
21 | Gachsaran 4 | P-102-A/B | Power (kW) | 1.35 | 1.35 | P.ME!E20 | Match
21 | Gachsaran 4 | P-102-A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
21 | Gachsaran 4 | P-102-A/B | Currency | EUR | EUR | P.ME!H20 | Match
21 | Gachsaran 4 | P-102-A/B | Unit Price | 15000 | 15000 | P.ME!H20 | Match
22 | Gachsaran 4 | P-105 | Equipment Name | DEAERATED WATER PUMPS | DEAERATED WATER PUMPS | P.ME!D21 | Match
22 | Gachsaran 4 | P-105 | Quantity | 1 | 1 | P.ME!G21 | Match
22 | Gachsaran 4 | P-105 | Pump Family | Centrifugal | (not stated) |  | Inferred – marked
22 | Gachsaran 4 | P-105 | Capacity (m³/h) | 40 | 40 | P.ME!E21 | Match
22 | Gachsaran 4 | P-105 | Discharge Pressure (barg) | 2.4 | 2.4 | P.ME!E21 | Match
22 | Gachsaran 4 | P-105 | Power (kW) | 2.7 | 2.7 | P.ME!E21 | Match
22 | Gachsaran 4 | P-105 | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
22 | Gachsaran 4 | P-105 | Currency | EUR | EUR | P.ME!H21 | Match
22 | Gachsaran 4 | P-105 | Unit Price | 17000 | 17000 | P.ME!H21 | Match
23 | Gachsaran 4 | P-104 | Equipment Name | POTABLE WATER FILLING PUMP | POTABLE WATER FILLING PUMP | P.ME!D23 | Match
23 | Gachsaran 4 | P-104 | Quantity | 1 | 1 | P.ME!G23 | Match
23 | Gachsaran 4 | P-104 | Pump Family | Centrifugal | (not stated) |  | Inferred – marked
23 | Gachsaran 4 | P-104 | Capacity (m³/h) | 20 | 20 | P.ME!E23 | Match
23 | Gachsaran 4 | P-104 | Discharge Pressure (barg) | 2.5 | 2.5 | P.ME!E23 | Match
23 | Gachsaran 4 | P-104 | Power (kW) | 1.4 | 1.4 | P.ME!E23 | Match
23 | Gachsaran 4 | P-104 | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
23 | Gachsaran 4 | P-104 | Currency | EUR | EUR | P.ME!H23 | Match
23 | Gachsaran 4 | P-104 | Unit Price | 11000 | 11000 | P.ME!H23 | Match
24 | Gachsaran 4 | P-201-A/B/C | Equipment Name | WATER INJECTION MAIN PUMPS | WATER INJECTION MAIN PUMPS | P.ME!D24 | Match
24 | Gachsaran 4 | P-201-A/B/C | Quantity | 3 | 3 | P.ME!G24 | Match
24 | Gachsaran 4 | P-201-A/B/C | Pump Family | Centrifugal | (not stated) |  | Inferred – marked
24 | Gachsaran 4 | P-201-A/B/C | Capacity (m³/h) | 73 | 73 | P.ME!E24 | Match
24 | Gachsaran 4 | P-201-A/B/C | Discharge Pressure (barg) | 36.3 | 36.3 | P.ME!E24 | Match
24 | Gachsaran 4 | P-201-A/B/C | Power (kW) | 73.6 | 73.6 | P.ME!E24 | Match
24 | Gachsaran 4 | P-201-A/B/C | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
24 | Gachsaran 4 | P-201-A/B/C | Currency | EUR | EUR | P.ME!H24 | Match
24 | Gachsaran 4 | P-201-A/B/C | Unit Price | 430000 | 430000 | P.ME!H24 | Match
25 | Gachsaran 4 | P-206-A/B/C | Equipment Name | WATER INJECTION BOOSTER PUMPS | WATER INJECTION BOOSTER PUMPS | P.ME!D25 | Match
25 | Gachsaran 4 | P-206-A/B/C | Quantity | 3 | 3 | P.ME!G25 | Match
25 | Gachsaran 4 | P-206-A/B/C | Pump Family | Centrifugal | (not stated) |  | Inferred – marked
25 | Gachsaran 4 | P-206-A/B/C | Capacity (m³/h) | 36.5 | 36.5 | P.ME!E25 | Match
25 | Gachsaran 4 | P-206-A/B/C | Discharge Pressure (barg) | 36.3 | 36.3 | P.ME!E25 | Match
25 | Gachsaran 4 | P-206-A/B/C | Power (kW) | 36.5 | 36.5 | P.ME!E25 | Match
25 | Gachsaran 4 | P-206-A/B/C | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
25 | Gachsaran 4 | P-206-A/B/C | Currency | EUR | EUR | P.ME!H25 | Match
25 | Gachsaran 4 | P-206-A/B/C | Unit Price | 285000 | 285000 | P.ME!H25 | Match
26 | Gachsaran 4 | P-501-A/B/C | Equipment Name | CHEMICAL INJECTION PORTABLE PUMPS | CHEMICAL INJECTION PORTABLE PUMPS | P.ME!D36 | Match
26 | Gachsaran 4 | P-501-A/B/C | Quantity | 3 | 3 | P.ME!G36 | Match
26 | Gachsaran 4 | P-501-A/B/C | Pump Family | Centrifugal | (not stated) |  | Inferred – marked
26 | Gachsaran 4 | P-501-A/B/C | Discharge Pressure (barg) | 2 | 2 | P.ME!E36 | Match
26 | Gachsaran 4 | P-501-A/B/C | Power (kW) | 0.45 | 0.45 | P.ME!E36 | Match
26 | Gachsaran 4 | P-501-A/B/C | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
26 | Gachsaran 4 | P-501-A/B/C | Currency | EUR | EUR | P.ME!H36 | Match
26 | Gachsaran 4 | P-501-A/B/C | Unit Price | 9000 | 9000 | P.ME!H36 | Match
27 | Gachsaran 4 | P-601-A/B | Equipment Name | FLARE K.O DRUM LIQUID PUMPS | FLARE K.O DRUM LIQUID PUMPS | P.ME!D46 | Match
27 | Gachsaran 4 | P-601-A/B | Quantity | 2 | 2 | P.ME!G46 | Match
27 | Gachsaran 4 | P-601-A/B | Pump Family | Centrifugal | (not stated) |  | Inferred – marked
27 | Gachsaran 4 | P-601-A/B | Capacity (m³/h) | 15 | 15 | P.ME!E46 | Match
27 | Gachsaran 4 | P-601-A/B | Discharge Pressure (barg) | 0.8 | 0.8 | P.ME!E46 | Match
27 | Gachsaran 4 | P-601-A/B | Power (kW) | 0.33 | 0.33 | P.ME!E46 | Match
27 | Gachsaran 4 | P-601-A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
27 | Gachsaran 4 | P-601-A/B | Currency | EUR | EUR | P.ME!H46 | Match
27 | Gachsaran 4 | P-601-A/B | Unit Price | 28000 | 28000 | P.ME!H46 | Match
28 | Gachsaran 4 | P-701-A/B | Equipment Name | HC CLOSED DRAIN TRANSFER PUMPS | HC CLOSED DRAIN TRANSFER PUMPS | P.ME!D50 | Match
28 | Gachsaran 4 | P-701-A/B | Quantity | 2 | 2 | P.ME!G50 | Match
28 | Gachsaran 4 | P-701-A/B | Pump Family | Centrifugal | (not stated) |  | Inferred – marked
28 | Gachsaran 4 | P-701-A/B | Capacity (m³/h) | 27.5 | 27.5 | P.ME!E50 | Match
28 | Gachsaran 4 | P-701-A/B | Discharge Pressure (barg) | 4.3 | 4.3 | P.ME!E50 | Match
28 | Gachsaran 4 | P-701-A/B | Power (kW) | 3.3 | 3.3 | P.ME!E50 | Match
28 | Gachsaran 4 | P-701-A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
28 | Gachsaran 4 | P-701-A/B | Currency | EUR | EUR | P.ME!H50 | Match
28 | Gachsaran 4 | P-701-A/B | Unit Price | 53000 | 53000 | P.ME!H50 | Match
29 | Gachsaran 4 | P-702A/B | Equipment Name | HC CLOSED DRAIN DRUM SUMP PUMP | HC CLOSED DRAIN DRUM SUMP PUMP | P.ME!D51 | Match
29 | Gachsaran 4 | P-702A/B | Quantity | 2 | 2 | P.ME!G51 | Match
29 | Gachsaran 4 | P-702A/B | Pump Family | Centrifugal | (not stated) |  | Inferred – marked
29 | Gachsaran 4 | P-702A/B | Capacity (m³/h) | 5.5 | 5.5 | P.ME!E51 | Match
29 | Gachsaran 4 | P-702A/B | Discharge Pressure (barg) | 7 | 7 | P.ME!E51 | Match
29 | Gachsaran 4 | P-702A/B | Power (kW) | 0.11 | 0.11 | P.ME!E51 | Match
29 | Gachsaran 4 | P-702A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
29 | Gachsaran 4 | P-702A/B | Currency | EUR | EUR | P.ME!H51 | Match
29 | Gachsaran 4 | P-702A/B | Unit Price | 53000 | 53000 | P.ME!H51 | Match
30 | Gachsaran 4 | P-703-A/B | Equipment Name | CLEAN WATER PUMPS | CLEAN WATER PUMPS | P.ME!D53 | Match
30 | Gachsaran 4 | P-703-A/B | Quantity | 2 | 2 | P.ME!G53 | Match
30 | Gachsaran 4 | P-703-A/B | Pump Family | Centrifugal | (not stated) |  | Inferred – marked
30 | Gachsaran 4 | P-703-A/B | Capacity (m³/h) | 11 | 11 | P.ME!E53 | Match
30 | Gachsaran 4 | P-703-A/B | Discharge Pressure (barg) | 1.8 | 1.8 | P.ME!E53 | Match
30 | Gachsaran 4 | P-703-A/B | Power (kW) | 0.54 | 0.54 | P.ME!E53 | Match
30 | Gachsaran 4 | P-703-A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
30 | Gachsaran 4 | P-703-A/B | Currency | EUR | EUR | P.ME!H53 | Match
30 | Gachsaran 4 | P-703-A/B | Unit Price | 29000 | 29000 | P.ME!H53 | Match
31 | Gachsaran 4 | P-704-A/B | Equipment Name | RECOVERED WASTE OIL PUMPS | RECOVERED WASTE OIL PUMPS | P.ME!D54 | Match
31 | Gachsaran 4 | P-704-A/B | Quantity | 2 | 2 | P.ME!G54 | Match
31 | Gachsaran 4 | P-704-A/B | Pump Family | Centrifugal | (not stated) |  | Inferred – marked
31 | Gachsaran 4 | P-704-A/B | Capacity (m³/h) | 11 | 11 | P.ME!E54 | Match
31 | Gachsaran 4 | P-704-A/B | Discharge Pressure (barg) | 2.7 | 2.7 | P.ME!E54 | Match
31 | Gachsaran 4 | P-704-A/B | Power (kW) | 0.8 | 0.8 | P.ME!E54 | Match
31 | Gachsaran 4 | P-704-A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
31 | Gachsaran 4 | P-704-A/B | Currency | EUR | EUR | P.ME!H54 | Match
31 | Gachsaran 4 | P-704-A/B | Unit Price | 35000 | 35000 | P.ME!H54 | Match
32 | Gachsaran 4 | P-750 | Equipment Name | OILY WATER SEPARATOR PUMP | OILY WATER SEPARATOR PUMP | P.ME!D55 | Match
32 | Gachsaran 4 | P-750 | Quantity | 1 | 1 | P.ME!G55 | Match
32 | Gachsaran 4 | P-750 | Pump Family | Centrifugal | (not stated) |  | Inferred – marked
32 | Gachsaran 4 | P-750 | Capacity (m³/h) | 1 | 1 | P.ME!E55 | Match
32 | Gachsaran 4 | P-750 | Discharge Pressure (barg) | 0.84 | 0.84 | P.ME!E55 | Match
32 | Gachsaran 4 | P-750 | Power (kW) | 0.02 | 0.02 | P.ME!E55 | Match
32 | Gachsaran 4 | P-750 | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
32 | Gachsaran 4 | P-750 | Currency | EUR | EUR | P.ME!H55 | Match
32 | Gachsaran 4 | P-750 | Unit Price | 13350 | 13350 | P.ME!H55 | Match
33 | Gachsaran 4 | P-705-A/B | Equipment Name | DIRTY OIL PUMPS | DIRTY OIL PUMPS | P.ME!D57 | Match
33 | Gachsaran 4 | P-705-A/B | Quantity | 2 | 2 | P.ME!G57 | Match
33 | Gachsaran 4 | P-705-A/B | Pump Family | Centrifugal | (not stated) |  | Inferred – marked
33 | Gachsaran 4 | P-705-A/B | Capacity (m³/h) | 5 | 5 | P.ME!E57 | Match
33 | Gachsaran 4 | P-705-A/B | Discharge Pressure (barg) | 2 | 2 | P.ME!E57 | Match
33 | Gachsaran 4 | P-705-A/B | Power (kW) | 0.3 | 0.3 | P.ME!E57 | Match
33 | Gachsaran 4 | P-705-A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
33 | Gachsaran 4 | P-705-A/B | Currency | EUR | EUR | P.ME!H57 | Match
33 | Gachsaran 4 | P-705-A/B | Unit Price | 31000 | 31000 | P.ME!H57 | Match
34 | Gachsaran 4 | P-706-A/B | Equipment Name | RECOVERED WASTE WATER PUMPS | RECOVERED WASTE WATER PUMPS | P.ME!D58 | Match
34 | Gachsaran 4 | P-706-A/B | Quantity | 2 | 2 | P.ME!G58 | Match
34 | Gachsaran 4 | P-706-A/B | Pump Family | Centrifugal | (not stated) |  | Inferred – marked
34 | Gachsaran 4 | P-706-A/B | Capacity (m³/h) | 33 | 33 | P.ME!E58 | Match
34 | Gachsaran 4 | P-706-A/B | Discharge Pressure (barg) | 1.5 | 1.5 | P.ME!E58 | Match
34 | Gachsaran 4 | P-706-A/B | Power (kW) | 1.35 | 1.35 | P.ME!E58 | Match
34 | Gachsaran 4 | P-706-A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
34 | Gachsaran 4 | P-706-A/B | Currency | EUR | EUR | P.ME!H58 | Match
34 | Gachsaran 4 | P-706-A/B | Unit Price | 28000 | 28000 | P.ME!H58 | Match
35 | Gachsaran 4 | P-801 | Equipment Name | DIESEL OIL PUMP | DIESEL OIL PUMP | P.ME!D60 | Match
35 | Gachsaran 4 | P-801 | Quantity | 1 | 1 | P.ME!G60 | Match
35 | Gachsaran 4 | P-801 | Pump Family | Centrifugal | (not stated) |  | Inferred – marked
35 | Gachsaran 4 | P-801 | Capacity (m³/h) | 10 | 10 | P.ME!E60 | Match
35 | Gachsaran 4 | P-801 | Discharge Pressure (barg) | 0.6 | 0.6 | P.ME!E60 | Match
35 | Gachsaran 4 | P-801 | Power (kW) | 0.16 | 0.16 | P.ME!E60 | Match
35 | Gachsaran 4 | P-801 | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
35 | Gachsaran 4 | P-801 | Currency | EUR | EUR | P.ME!H60 | Match
35 | Gachsaran 4 | P-801 | Unit Price | 13500 | 13500 | P.ME!H60 | Match
36 | Gachsaran 4 | P-901A/B | Equipment Name | FIRE WATER MAIN ELECTRICAL PUMP | FIRE WATER MAIN ELECTRICAL PUMP | P.ME!D61 | Match
36 | Gachsaran 4 | P-901A/B | Quantity | 2 | 2 | P.ME!G61 | Match
36 | Gachsaran 4 | P-901A/B | Pump Family | Centrifugal | (not stated) |  | Inferred – marked
36 | Gachsaran 4 | P-901A/B | Capacity (m³/h) | 480 | 480 | P.ME!E61 | Match
36 | Gachsaran 4 | P-901A/B | Discharge Pressure (barg) | 10 | 10 | P.ME!E61 | Match
36 | Gachsaran 4 | P-901A/B | Power (kW) | 133 | 133 | P.ME!E61 | Match
36 | Gachsaran 4 | P-901A/B | Driver Type | Electric Motor | name: electric | Equipment Name | Match
36 | Gachsaran 4 | P-901A/B | Currency | IRR | IRR | P.ME!H61 | Match
36 | Gachsaran 4 | P-901A/B | Unit Price | 37500000000 | 37500000000 | P.ME!H61 | Match
37 | Gachsaran 4 | P902 | Equipment Name | FIRE WATER MAIN DESEL PUMP | FIRE WATER MAIN DESEL PUMP | P.ME!D62 | Match
37 | Gachsaran 4 | P902 | Quantity | 1 | 1 | P.ME!G62 | Match
37 | Gachsaran 4 | P902 | Pump Family | Centrifugal | (not stated) |  | Inferred – marked
37 | Gachsaran 4 | P902 | Capacity (m³/h) | 480 | 480 | P.ME!E62 | Match
37 | Gachsaran 4 | P902 | Discharge Pressure (barg) | 10 | 10 | P.ME!E62 | Match
37 | Gachsaran 4 | P902 | Power (kW) | 133 | 133 | P.ME!E62 | Match
37 | Gachsaran 4 | P902 | Driver Type | Diesel Engine | name: diesel | Equipment Name | Match
37 | Gachsaran 4 | P902 | Currency | IRR | IRR | P.ME!H62 | Match
37 | Gachsaran 4 | P902 | Unit Price | 45000000000 | 45000000000 | P.ME!H62 | Match
38 | Gachsaran 4 | P-903-A/B | Equipment Name | FIRE WATER JOCKEY PUMPS | FIRE WATER JOCKEY PUMPS | P.ME!D63 | Match
38 | Gachsaran 4 | P-903-A/B | Quantity | 2 | 2 | P.ME!G63 | Match
38 | Gachsaran 4 | P-903-A/B | Pump Family | Centrifugal | (not stated) |  | Inferred – marked
38 | Gachsaran 4 | P-903-A/B | Capacity (m³/h) | 15 | 15 | P.ME!E63 | Match
38 | Gachsaran 4 | P-903-A/B | Discharge Pressure (barg) | 6 | 6 | P.ME!E63 | Match
38 | Gachsaran 4 | P-903-A/B | Power (kW) | 2.5 | 2.5 | P.ME!E63 | Match
38 | Gachsaran 4 | P-903-A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
38 | Gachsaran 4 | P-903-A/B | Currency | IRR | IRR | P.ME!H63 | Match
38 | Gachsaran 4 | P-903-A/B | Unit Price | 2000000000 | 2000000000 | P.ME!H63 | Match
39 | Gachsaran 4 | P108A/B | Equipment Name | UNIT SUPPLY WATER PUMP | UNIT SUPPLY WATER PUMP | P.ME!D64 | Match
39 | Gachsaran 4 | P108A/B | Quantity | 2 | 2 | P.ME!G64 | Match
39 | Gachsaran 4 | P108A/B | Pump Family | Centrifugal | (not stated) |  | Inferred – marked
39 | Gachsaran 4 | P108A/B | Capacity (m³/h) | 15 | 15 | P.ME!E64 | Match
39 | Gachsaran 4 | P108A/B | Discharge Pressure (barg) | 6 | 6 | P.ME!E64 | Match
39 | Gachsaran 4 | P108A/B | Power (kW) | 2.5 | 2.5 | P.ME!E64 | Match
39 | Gachsaran 4 | P108A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
39 | Gachsaran 4 | P108A/B | Currency | EUR | EUR | P.ME!H64 | Match
39 | Gachsaran 4 | P108A/B | Unit Price | 17500 | 17500 | P.ME!H64 | Match
40 | Gachsaran 4 | P-904 | Equipment Name | FIRE WATER LOADING PUMP | FIRE WATER LOADING PUMP | P.ME!D68 | Match
40 | Gachsaran 4 | P-904 | Quantity | 1 | 1 | P.ME!G68 | Match
40 | Gachsaran 4 | P-904 | Pump Family | Centrifugal | (not stated) |  | Inferred – marked
40 | Gachsaran 4 | P-904 | Capacity (m³/h) | 30 | 30 | P.ME!E68 | Match
40 | Gachsaran 4 | P-904 | Discharge Pressure (barg) | 3 | 3 | P.ME!E68 | Match
40 | Gachsaran 4 | P-904 | Power (kW) | 2.5 | 2.5 | P.ME!E68 | Match
40 | Gachsaran 4 | P-904 | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
40 | Gachsaran 4 | P-904 | Currency | EUR | EUR | P.ME!H68 | Match
40 | Gachsaran 4 | P-904 | Unit Price | 19500 | 19500 | P.ME!H68 | Match
41 | Koopal Asmari | P-111 A/B/C | Equipment Name | Salty Crude Transfer Pumps | Salty Crude Transfer Pumps | PUMPS-A (1)!F19 | Match
41 | Koopal Asmari | P-111 A/B/C | Quantity | 3 | 3 | PUMPS-A (1)!R19 | Match
41 | Koopal Asmari | P-111 A/B/C | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS-A (1)!F20 | Match
41 | Koopal Asmari | P-111 A/B/C | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS-A (1)!F20 | Match
41 | Koopal Asmari | P-111 A/B/C | Material Class | D-1 | D1 | PUMPS-A (1)!F24 | Match
41 | Koopal Asmari | P-111 A/B/C | Capacity (m³/h) | 354 | 354 | PUMPS-A (1)!F21 | Match
41 | Koopal Asmari | P-111 A/B/C | Diff. Head (m) | 31.2 | 31.2 | PUMPS-A (1)!F22 | Match
41 | Koopal Asmari | P-111 A/B/C | Discharge Pressure (barg) | 4 | 4 | PUMPS-A (1)!F23 | Match
41 | Koopal Asmari | P-111 A/B/C | NACE | N | (no NACE line) |  | Inferred – marked
41 | Koopal Asmari | P-111 A/B/C | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS-A (1)!F25 | Match
41 | Koopal Asmari | P-111 A/B/C | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
41 | Koopal Asmari | P-111 A/B/C | Currency | EUR | EUR | PUMPS-A (1)!AK19 | Match
41 | Koopal Asmari | P-111 A/B/C | Unit Price | 55000 | 55000 | PUMPS-A (1)!AK19 | Match
42 | Koopal Asmari | P-114 A/B/C | Equipment Name | Salty Crude Booster Pumps | Salty Crude Booster Pumps | PUMPS-A (1)!F27 | Match
42 | Koopal Asmari | P-114 A/B/C | Quantity | 3 | 3 | PUMPS-A (1)!R27 | Match
42 | Koopal Asmari | P-114 A/B/C | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS-A (1)!F28 | Match
42 | Koopal Asmari | P-114 A/B/C | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS-A (1)!F28 | Match
42 | Koopal Asmari | P-114 A/B/C | Material Class | D-1 | D1 | PUMPS-A (1)!F32 | Match
42 | Koopal Asmari | P-114 A/B/C | Capacity (m³/h) | 255 | 255 | PUMPS-A (1)!F29 | Match
42 | Koopal Asmari | P-114 A/B/C | Diff. Head (m) | 170 | 170 | PUMPS-A (1)!F30 | Match
42 | Koopal Asmari | P-114 A/B/C | Discharge Pressure (barg) | 17.2 | 17.2 | PUMPS-A (1)!F31 | Match
42 | Koopal Asmari | P-114 A/B/C | NACE | N | (no NACE line) |  | Inferred – marked
42 | Koopal Asmari | P-114 A/B/C | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS-A (1)!F33 | Match
42 | Koopal Asmari | P-114 A/B/C | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
42 | Koopal Asmari | P-114 A/B/C | Currency | EUR | EUR | PUMPS-A (1)!AK27 | Match
42 | Koopal Asmari | P-114 A/B/C | Unit Price | 60000 | 60000 | PUMPS-A (1)!AK27 | Match
43 | Koopal Asmari | P-135 A/B | Equipment Name | Dirty Oil Pumps | Dirty Oil Pumps | PUMPS-A (1)!F35 | Match
43 | Koopal Asmari | P-135 A/B | Quantity | 2 | 2 | PUMPS-A (1)!R35 | Match
43 | Koopal Asmari | P-135 A/B | Pump Family | PD-Rotary (Gear) | P.D.-Rotary (Ext. Gear) | PUMPS-A (1)!F36 | Match
43 | Koopal Asmari | P-135 A/B | Material Class | D-1 | D1 | PUMPS-A (1)!F39 | Match
43 | Koopal Asmari | P-135 A/B | Capacity (m³/h) | 5 | 5 | PUMPS-A (1)!F37 | Match
43 | Koopal Asmari | P-135 A/B | Discharge Pressure (barg) | 5.3 | 5.3 | PUMPS-A (1)!F38 | Match
43 | Koopal Asmari | P-135 A/B | NACE | N | (no NACE line) |  | Inferred – marked
43 | Koopal Asmari | P-135 A/B | Standard / IPS | API 676 + IPS-M-PM-140 | API 676 & IPS-M-PM-140 | PUMPS-A (1)!F40 | Match
43 | Koopal Asmari | P-135 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
43 | Koopal Asmari | P-135 A/B | Currency | EUR | EUR | PUMPS-A (1)!AK35 | Match
43 | Koopal Asmari | P-135 A/B | Unit Price | 10000 | 10000 | PUMPS-A (1)!AK35 | Match
44 | Koopal Asmari | P-136 A/B | Equipment Name | Free Water Transfer Pumps | Free Water Transfer Pumps | PUMPS-A (1)!F42 | Match
44 | Koopal Asmari | P-136 A/B | Quantity | 2 | 2 | PUMPS-A (1)!R42 | Match
44 | Koopal Asmari | P-136 A/B | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS-A (1)!F43 | Match
44 | Koopal Asmari | P-136 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS-A (1)!F43 | Match
44 | Koopal Asmari | P-136 A/B | Material Class | D-2 | D2 | PUMPS-A (1)!F47 | Match
44 | Koopal Asmari | P-136 A/B | Capacity (m³/h) | 21 | 21 | PUMPS-A (1)!F44 | Match
44 | Koopal Asmari | P-136 A/B | Diff. Head (m) | 27.6 | 27.6 | PUMPS-A (1)!F45 | Match
44 | Koopal Asmari | P-136 A/B | Discharge Pressure (barg) | 4 | 4 | PUMPS-A (1)!F46 | Match
44 | Koopal Asmari | P-136 A/B | NACE | N | (no NACE line) |  | Inferred – marked
44 | Koopal Asmari | P-136 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS-A (1)!F48 | Match
44 | Koopal Asmari | P-136 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
44 | Koopal Asmari | P-136 A/B | Currency | EUR | EUR | PUMPS-A (1)!AK42 | Match
44 | Koopal Asmari | P-136 A/B | Unit Price | 30000 | 30000 | PUMPS-A (1)!AK42 | Match
45 | Koopal Asmari | P-137 A/B | Equipment Name | Disposal Water Injection Main Pumps | Disposal Water Injection Main Pumps | INS-PUMP-A (1)!AQ29 | Match (INS-PUMP sheet name)
45 | Koopal Asmari | P-137 A/B | Quantity | 2 | 2 | PUMPS-A (2)!R19 | Match
45 | Koopal Asmari | P-137 A/B | API 610 Type | BB3 | Centrifugal (BB3) | PUMPS-A (2)!F20 | Match
45 | Koopal Asmari | P-137 A/B | Pump Family | Centrifugal | Centrifugal (BB3) | PUMPS-A (2)!F20 | Match
45 | Koopal Asmari | P-137 A/B | Material Class | D-2 | D2 | PUMPS-A (2)!F24 | Match
45 | Koopal Asmari | P-137 A/B | Capacity (m³/h) | 73 | 73 | PUMPS-A (2)!F21 | Match
45 | Koopal Asmari | P-137 A/B | Diff. Head (m) | 607.4 | 607.4 | PUMPS-A (2)!F22 | Match
45 | Koopal Asmari | P-137 A/B | Discharge Pressure (barg) | 74.4 | 74.4 | PUMPS-A (2)!F23 | Match
45 | Koopal Asmari | P-137 A/B | NACE | N | (no NACE line) |  | Inferred – marked
45 | Koopal Asmari | P-137 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS-A (2)!F25 | Match
45 | Koopal Asmari | P-137 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
45 | Koopal Asmari | P-137 A/B | Currency | EUR | EUR | PUMPS-A (2)!AK19 | Match
45 | Koopal Asmari | P-137 A/B | Unit Price | 210000 | 210000 | PUMPS-A (2)!AK19 | Match
46 | Koopal Asmari | P-139 A/B | Equipment Name | Disposal Water Injection Booster Pumps | Disposal Water Injection Booster Pumps | INS-PUMP-A (1)!AQ31 | Match (INS-PUMP sheet name)
46 | Koopal Asmari | P-139 A/B | Quantity | 2 | 2 | PUMPS-A (2)!R27 | Match
46 | Koopal Asmari | P-139 A/B | API 610 Type | BB3 | Centrifugal (BB3) | PUMPS-A (2)!F28 | Match
46 | Koopal Asmari | P-139 A/B | Pump Family | Centrifugal | Centrifugal (BB3) | PUMPS-A (2)!F28 | Match
46 | Koopal Asmari | P-139 A/B | Material Class | D-2 | D2 | PUMPS-A (2)!F32 | Match
46 | Koopal Asmari | P-139 A/B | Capacity (m³/h) | 36 | 36 | PUMPS-A (2)!F29 | Match
46 | Koopal Asmari | P-139 A/B | Diff. Head (m) | 331 | 331 | PUMPS-A (2)!F30 | Match
46 | Koopal Asmari | P-139 A/B | Discharge Pressure (barg) | 37.4 | 37.4 | PUMPS-A (2)!F31 | Match
46 | Koopal Asmari | P-139 A/B | NACE | N | (no NACE line) |  | Inferred – marked
46 | Koopal Asmari | P-139 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS-A (2)!F33 | Match
46 | Koopal Asmari | P-139 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
46 | Koopal Asmari | P-139 A/B | Currency | EUR | EUR | PUMPS-A (2)!AK27 | Match
46 | Koopal Asmari | P-139 A/B | Unit Price | 150000 | 150000 | PUMPS-A (2)!AK27 | Match
47 | Koopal Asmari | P-151 A/B | Equipment Name | Dilution Water Pumps | Dilution Water Pumps | PUMPS-A (2)!F35 | Match
47 | Koopal Asmari | P-151 A/B | Quantity | 2 | 2 | PUMPS-A (2)!R35 | Match
47 | Koopal Asmari | P-151 A/B | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS-A (2)!F36 | Match
47 | Koopal Asmari | P-151 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS-A (2)!F36 | Match
47 | Koopal Asmari | P-151 A/B | Material Class | S-5 | S5 | PUMPS-A (2)!F40 | Match
47 | Koopal Asmari | P-151 A/B | Capacity (m³/h) | 23 | 23 | PUMPS-A (2)!F37 | Match
47 | Koopal Asmari | P-151 A/B | Diff. Head (m) | 158 | 158 | PUMPS-A (2)!F38 | Match
47 | Koopal Asmari | P-151 A/B | Discharge Pressure (barg) | 16.7 | 16.7 | PUMPS-A (2)!F39 | Match
47 | Koopal Asmari | P-151 A/B | NACE | N | (no NACE line) |  | Inferred – marked
47 | Koopal Asmari | P-151 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS-A (2)!F41 | Match
47 | Koopal Asmari | P-151 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
47 | Koopal Asmari | P-151 A/B | Currency | EUR | EUR | PUMPS-A (2)!AK35 | Match
47 | Koopal Asmari | P-151 A/B | Unit Price | 16500 | 16500 | PUMPS-A (2)!AK35 | Match
48 | Koopal Asmari | P-152 | Equipment Name | Dilution Water Pump | Dilution Water Pump | PUMPS-A (2)!F43 | Match
48 | Koopal Asmari | P-152 | Quantity | 1 | 1 | PUMPS-A (2)!R43 | Match
48 | Koopal Asmari | P-152 | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS-A (2)!F44 | Match
48 | Koopal Asmari | P-152 | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS-A (2)!F44 | Match
48 | Koopal Asmari | P-152 | Material Class | S-5 | S5 | PUMPS-A (2)!F48 | Match
48 | Koopal Asmari | P-152 | Capacity (m³/h) | 43 | 43 | PUMPS-A (2)!F45 | Match
48 | Koopal Asmari | P-152 | Diff. Head (m) | 158 | 158 | PUMPS-A (2)!F46 | Match
48 | Koopal Asmari | P-152 | Discharge Pressure (barg) | 16.7 | 16.7 | PUMPS-A (2)!F47 | Match
48 | Koopal Asmari | P-152 | NACE | N | (no NACE line) |  | Inferred – marked
48 | Koopal Asmari | P-152 | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS-A (2)!F49 | Match
48 | Koopal Asmari | P-152 | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
48 | Koopal Asmari | P-152 | Currency | EUR | EUR | PUMPS-A (2)!AK43 | Match
48 | Koopal Asmari | P-152 | Unit Price | 17500 | 17500 | PUMPS-A (2)!AK43 | Match
49 | Koopal Asmari | P-171 A/B | Equipment Name | Flare K.O. Drum Pumps | Flare K.O. Drum Pumps | PUMPS-A (3)!F19 | Match
49 | Koopal Asmari | P-171 A/B | Quantity | 2 | 2 | PUMPS-A (3)!R19 | Match
49 | Koopal Asmari | P-171 A/B | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS-A (3)!F20 | Match
49 | Koopal Asmari | P-171 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS-A (3)!F20 | Match
49 | Koopal Asmari | P-171 A/B | Material Class | S-6 | S6 | PUMPS-A (3)!F24 | Match
49 | Koopal Asmari | P-171 A/B | Capacity (m³/h) | 15 | 15 | PUMPS-A (3)!F21 | Match
49 | Koopal Asmari | P-171 A/B | Diff. Head (m) | 50 | 50 | PUMPS-A (3)!F22 | Match
49 | Koopal Asmari | P-171 A/B | Discharge Pressure (barg) | 7.4 | 7.4 | PUMPS-A (3)!F23 | Match
49 | Koopal Asmari | P-171 A/B | NACE | N | (no NACE line) |  | Inferred – marked
49 | Koopal Asmari | P-171 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS-A (3)!F25 | Match
49 | Koopal Asmari | P-171 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
49 | Koopal Asmari | P-171 A/B | Currency | EUR | EUR | PUMPS-A (3)!AK19 | Match
49 | Koopal Asmari | P-171 A/B | Unit Price | 10000 | 10000 | PUMPS-A (3)!AK19 | Match
50 | Koopal Asmari | P-231 A/B | Equipment Name | O.W.S. Oil Pumps | O.W.S. Oil Pumps | PUMPS-A (3)!F27 | Match
50 | Koopal Asmari | P-231 A/B | Quantity | 2 | 2 | PUMPS-A (3)!R27 | Match
50 | Koopal Asmari | P-231 A/B | Pump Family | PD-Rotary (Progressing Cavity) | P.D.-Rotary (Progressing Cavity) | PUMPS-A (3)!F28 | Match
50 | Koopal Asmari | P-231 A/B | Material Class | D-1 | D1 | PUMPS-A (3)!F31 | Match
50 | Koopal Asmari | P-231 A/B | Capacity (m³/h) | 6 | 6 | PUMPS-A (3)!F29 | Match
50 | Koopal Asmari | P-231 A/B | Discharge Pressure (barg) | 3.6 | 3.6 | PUMPS-A (3)!F30 | Match
50 | Koopal Asmari | P-231 A/B | NACE | N | (no NACE line) |  | Inferred – marked
50 | Koopal Asmari | P-231 A/B | Standard / IPS | API 676 + IPS-M-PM-140 | API 676 & IPS-M-PM-140 | PUMPS-A (3)!F32 | Match
50 | Koopal Asmari | P-231 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
50 | Koopal Asmari | P-231 A/B | Currency | EUR | EUR | PUMPS-A (3)!AK27 | Match
50 | Koopal Asmari | P-231 A/B | Unit Price | 25000 | 25000 | PUMPS-A (3)!AK27 | Match
51 | Koopal Asmari | P-232 A/B | Equipment Name | O.W.S. Water Pumps | O.W.S. Water Pumps | PUMPS-A (3)!F34 | Match
51 | Koopal Asmari | P-232 A/B | Quantity | 2 | 2 | PUMPS-A (3)!R34 | Match
51 | Koopal Asmari | P-232 A/B | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS-A (3)!F35 | Match
51 | Koopal Asmari | P-232 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS-A (3)!F35 | Match
51 | Koopal Asmari | P-232 A/B | Material Class | D-2 | D2 | PUMPS-A (3)!F39 | Match
51 | Koopal Asmari | P-232 A/B | Capacity (m³/h) | 11 | 11 | PUMPS-A (3)!F36 | Match
51 | Koopal Asmari | P-232 A/B | Diff. Head (m) | 27.6 | 27.6 | PUMPS-A (3)!F37 | Match
51 | Koopal Asmari | P-232 A/B | Discharge Pressure (barg) | 3 | 3 | PUMPS-A (3)!F38 | Match
51 | Koopal Asmari | P-232 A/B | NACE | N | (no NACE line) |  | Inferred – marked
51 | Koopal Asmari | P-232 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS-A (3)!F40 | Match
51 | Koopal Asmari | P-232 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
51 | Koopal Asmari | P-232 A/B | Currency | EUR | EUR | PUMPS-A (3)!AK34 | Match
51 | Koopal Asmari | P-232 A/B | Unit Price | 20000 | 20000 | PUMPS-A (3)!AK34 | Match
52 | Koopal Asmari | P-234 A/B | Equipment Name | Closed Drain Drum Pumps | Closed Drain Drum Pumps | PUMPS-A (3)!F42 | Match
52 | Koopal Asmari | P-234 A/B | Quantity | 2 | 2 | PUMPS-A (3)!R42 | Match
52 | Koopal Asmari | P-234 A/B | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS-A (3)!F43 | Match
52 | Koopal Asmari | P-234 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS-A (3)!F43 | Match
52 | Koopal Asmari | P-234 A/B | Material Class | D-2 | D2 | PUMPS-A (3)!F47 | Match
52 | Koopal Asmari | P-234 A/B | Capacity (m³/h) | 15 | 15 | PUMPS-A (3)!F44 | Match
52 | Koopal Asmari | P-234 A/B | Diff. Head (m) | 46.81 | 46.81 | PUMPS-A (3)!F45 | Match
52 | Koopal Asmari | P-234 A/B | Discharge Pressure (barg) | 8.5 | 8.5 | PUMPS-A (3)!F46 | Match
52 | Koopal Asmari | P-234 A/B | NACE | N | (no NACE line) |  | Inferred – marked
52 | Koopal Asmari | P-234 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS-A (3)!F48 | Match
52 | Koopal Asmari | P-234 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
52 | Koopal Asmari | P-234 A/B | Currency | EUR | EUR | PUMPS-A (3)!AK42 | Match
52 | Koopal Asmari | P-234 A/B | Unit Price | 15000 | 15000 | PUMPS-A (3)!AK42 | Match
53 | Koopal Asmari | P-113 A/B | API 610 Type | OH2 | Centrifugal (OH2) | DESALTERS-A!F32 | Match
53 | Koopal Asmari | P-113 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | DESALTERS-A!F32 | Match
53 | Koopal Asmari | P-113 A/B | Material Class | D-2 | D2 | DESALTERS-A!F35 | Match
53 | Koopal Asmari | P-113 A/B | Capacity (m³/h) | 21 | 21 | DESALTERS-A!F33 | Match
53 | Koopal Asmari | P-113 A/B | Diff. Head (m) | 44.9 | ΔP 4.4 bar | DESALTERS-A!F34 | Derived – marked
53 | Koopal Asmari | P-113 A/B | NACE | N | (no NACE line) |  | Inferred – marked
53 | Koopal Asmari | P-113 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | DESALTERS-A!F36 | Match
53 | Koopal Asmari | P-113 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
53 | Koopal Asmari | P-113 A/B | Unit Price | (Not stated) | priced inside package | DESALTERS-A | Match
54 | Koopal Asmari | P-130 A/B | API 610 Type | OH2 | Centrifugal (OH2) | IWWTP-A (1)!F33 | Match
54 | Koopal Asmari | P-130 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | IWWTP-A (1)!F33 | Match
54 | Koopal Asmari | P-130 A/B | Material Class | D-2 | D2 | IWWTP-A (1)!F34 | Match
54 | Koopal Asmari | P-130 A/B | NACE | N | (no NACE line) |  | Inferred – marked
54 | Koopal Asmari | P-130 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | IWWTP-A (1)!F35 | Match
54 | Koopal Asmari | P-130 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
54 | Koopal Asmari | P-130 A/B | Unit Price | (Not stated) | priced inside package | IWWTP-A (1) | Match
55 | Koopal Asmari | P-131 A/B | API 610 Type | OH2 | Centrifugal (OH2) | IWWTP-A (1)!F38 | Match
55 | Koopal Asmari | P-131 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | IWWTP-A (1)!F38 | Match
55 | Koopal Asmari | P-131 A/B | Material Class | D-2 | D2 | IWWTP-A (1)!F39 | Match
55 | Koopal Asmari | P-131 A/B | NACE | N | (no NACE line) |  | Inferred – marked
55 | Koopal Asmari | P-131 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | IWWTP-A (1)!F40 | Match
55 | Koopal Asmari | P-131 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
55 | Koopal Asmari | P-131 A/B | Unit Price | (Not stated) | priced inside package | IWWTP-A (1) | Match
56 | Koopal Asmari | P-132 A/B | API 610 Type | OH2 | Centrifugal (OH2) | IWWTP-A (1)!F38 | Match
56 | Koopal Asmari | P-132 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | IWWTP-A (1)!F38 | Match
56 | Koopal Asmari | P-132 A/B | Material Class | D-2 | D2 | IWWTP-A (1)!F39 | Match
56 | Koopal Asmari | P-132 A/B | NACE | N | (no NACE line) |  | Inferred – marked
56 | Koopal Asmari | P-132 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | IWWTP-A (1)!F40 | Match
56 | Koopal Asmari | P-132 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
56 | Koopal Asmari | P-132 A/B | Unit Price | (Not stated) | priced inside package | IWWTP-A (1) | Match
57 | Koopal Asmari | P-133 A/B | Pump Family | PD-Rotary (Gear) | P.D.-Rotary (Ext. Gear) | IWWTP-A (1)!F43 | Match
57 | Koopal Asmari | P-133 A/B | Material Class | D-1 | D1 | IWWTP-A (1)!F44 | Match
57 | Koopal Asmari | P-133 A/B | NACE | N | (no NACE line) |  | Inferred – marked
57 | Koopal Asmari | P-133 A/B | Standard / IPS | API 676 + IPS-M-PM-140 | API 676 & IPS-M-PM-140 | IWWTP-A (1)!F45 | Match
57 | Koopal Asmari | P-133 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
57 | Koopal Asmari | P-133 A/B | Unit Price | (Not stated) | priced inside package | IWWTP-A (1) | Match
58 | Koopal Asmari | P-134 A/B | Pump Family | PD-Rotary (Screw) | P.D.-Rotary (Twin Screw) | IWWTP-A (2)!F17 | Match
58 | Koopal Asmari | P-134 A/B | Material Class | D-2 | D2 | IWWTP-A (2)!F18 | Match
58 | Koopal Asmari | P-134 A/B | NACE | N | (no NACE line) |  | Inferred – marked
58 | Koopal Asmari | P-134 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | IWWTP-A (2)!F19 | Match
58 | Koopal Asmari | P-134 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
58 | Koopal Asmari | P-134 A/B | Unit Price | (Not stated) | priced inside package | IWWTP-A (2) | Match
59 | Koopal Bangestan | P-121 A/B/C | Equipment Name | Salty Crude Transfer Pumps | Salty Crude Transfer Pumps | PUMPS-B!F19 | Match
59 | Koopal Bangestan | P-121 A/B/C | Quantity | 3 | 3 | PUMPS-B!R19 | Match
59 | Koopal Bangestan | P-121 A/B/C | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS-B!F20 | Match
59 | Koopal Bangestan | P-121 A/B/C | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS-B!F20 | Match
59 | Koopal Bangestan | P-121 A/B/C | Material Class | D-1 | D1 | PUMPS-B!F24 | Match
59 | Koopal Bangestan | P-121 A/B/C | Capacity (m³/h) | 186 | 186 | PUMPS-B!F21 | Match
59 | Koopal Bangestan | P-121 A/B/C | Diff. Head (m) | 33.4 | 33.4 | PUMPS-B!F22 | Match
59 | Koopal Bangestan | P-121 A/B/C | Discharge Pressure (barg) | 3.9 | 3.9 | PUMPS-B!F23 | Match
59 | Koopal Bangestan | P-121 A/B/C | NACE | Y | Y | PUMPS-B!F25 | Match
59 | Koopal Bangestan | P-121 A/B/C | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS-B!F26 | Match
59 | Koopal Bangestan | P-121 A/B/C | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
59 | Koopal Bangestan | P-121 A/B/C | Currency | EUR | EUR | PUMPS-B!AK19 | Match
59 | Koopal Bangestan | P-121 A/B/C | Unit Price | 55000 | 55000 | PUMPS-B!AK19 | Match
60 | Koopal Bangestan | P-122 A/B | Equipment Name | Off-Spec. Crude Pumps | Off-Spec. Crude Pumps | INS-PUMP-B (1)!AQ23 | Match (INS-PUMP sheet name)
60 | Koopal Bangestan | P-122 A/B | Quantity | 2 | 2 | PUMPS-B!R28 | Match
60 | Koopal Bangestan | P-122 A/B | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS-B!F29 | Match
60 | Koopal Bangestan | P-122 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS-B!F29 | Match
60 | Koopal Bangestan | P-122 A/B | Material Class | D-1 | D1 | PUMPS-B!F33 | Match
60 | Koopal Bangestan | P-122 A/B | Capacity (m³/h) | 37 | 37 | PUMPS-B!F30 | Match
60 | Koopal Bangestan | P-122 A/B | Diff. Head (m) | 39 | 39 | PUMPS-B!F31 | Match
60 | Koopal Bangestan | P-122 A/B | Discharge Pressure (barg) | 5.4 | 5.4 | PUMPS-B!F32 | Match
60 | Koopal Bangestan | P-122 A/B | NACE | Y | Y | PUMPS-B!F34 | Match
60 | Koopal Bangestan | P-122 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS-B!F35 | Match
60 | Koopal Bangestan | P-122 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
60 | Koopal Bangestan | P-122 A/B | Currency | EUR | EUR | PUMPS-B!AK28 | Match
60 | Koopal Bangestan | P-122 A/B | Unit Price | 15000 | 15000 | PUMPS-B!AK28 | Match
61 | Koopal Bangestan | P-124 A/B/C | Equipment Name | Salty Crude Booster Pumps | Salty Crude Booster Pumps | PUMPS-B!F37 | Match
61 | Koopal Bangestan | P-124 A/B/C | Quantity | 3 | 3 | PUMPS-B!R37 | Match
61 | Koopal Bangestan | P-124 A/B/C | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS-B!F38 | Match
61 | Koopal Bangestan | P-124 A/B/C | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS-B!F38 | Match
61 | Koopal Bangestan | P-124 A/B/C | Material Class | D-1 | D1 | PUMPS-B!F42 | Match
61 | Koopal Bangestan | P-124 A/B/C | Capacity (m³/h) | 173 | 173 | PUMPS-B!F39 | Match
61 | Koopal Bangestan | P-124 A/B/C | Diff. Head (m) | 186.3 | 186.3 | PUMPS-B!F40 | Match
61 | Koopal Bangestan | P-124 A/B/C | Discharge Pressure (barg) | 18 | 18 | PUMPS-B!F41 | Match
61 | Koopal Bangestan | P-124 A/B/C | NACE | Y | Y | PUMPS-B!F43 | Match
61 | Koopal Bangestan | P-124 A/B/C | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS-B!F44 | Match
61 | Koopal Bangestan | P-124 A/B/C | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
61 | Koopal Bangestan | P-124 A/B/C | Currency | EUR | EUR | PUMPS-B!AK37 | Match
61 | Koopal Bangestan | P-124 A/B/C | Unit Price | 60000 | 60000 | PUMPS-B!AK37 | Match
62 | Koopal Bangestan | P-145 A/B | Equipment Name | Dirty Oil Pumps | Dirty Oil Pumps | PUMPS-B (2)!F19 | Match
62 | Koopal Bangestan | P-145 A/B | Quantity | 2 | 2 | PUMPS-B (2)!R19 | Match
62 | Koopal Bangestan | P-145 A/B | Pump Family | PD-Rotary (Gear) | P.D.-Rotary (Ext. Gear) | PUMPS-B (2)!F20 | Match
62 | Koopal Bangestan | P-145 A/B | Material Class | D-1 | D1 | PUMPS-B (2)!F23 | Match
62 | Koopal Bangestan | P-145 A/B | Capacity (m³/h) | 5 | 5 | PUMPS-B (2)!F21 | Match
62 | Koopal Bangestan | P-145 A/B | Discharge Pressure (barg) | 6.5 | 6.5 | PUMPS-B (2)!F22 | Match
62 | Koopal Bangestan | P-145 A/B | NACE | Y | Y | PUMPS-B (2)!F24 | Match
62 | Koopal Bangestan | P-145 A/B | Standard / IPS | API 676 + IPS-M-PM-140 | API 676 & IPS-M-PM-140 | PUMPS-B (2)!F25 | Match
62 | Koopal Bangestan | P-145 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
62 | Koopal Bangestan | P-145 A/B | Currency | EUR | EUR | PUMPS-B (2)!AK19 | Match
62 | Koopal Bangestan | P-145 A/B | Unit Price | 10000 | 10000 | PUMPS-B (2)!AK19 | Match
63 | Koopal Bangestan | P-146 A/B | Equipment Name | Free Water Transfer Pumps | Free Water Transfer Pumps | PUMPS-B (2)!F27 | Match
63 | Koopal Bangestan | P-146 A/B | Quantity | 2 | 2 | PUMPS-B (2)!R27 | Match
63 | Koopal Bangestan | P-146 A/B | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS-B (2)!F28 | Match
63 | Koopal Bangestan | P-146 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS-B (2)!F28 | Match
63 | Koopal Bangestan | P-146 A/B | Material Class | D-2 | D2 | PUMPS-B (2)!F32 | Match
63 | Koopal Bangestan | P-146 A/B | Capacity (m³/h) | 14.5 | 14.5 | PUMPS-B (2)!F29 | Match
63 | Koopal Bangestan | P-146 A/B | Diff. Head (m) | 27.6 | 27.6 | PUMPS-B (2)!F30 | Match
63 | Koopal Bangestan | P-146 A/B | Discharge Pressure (barg) | 4 | 4 | PUMPS-B (2)!F31 | Match
63 | Koopal Bangestan | P-146 A/B | NACE | Y | Y | PUMPS-B (2)!F33 | Match
63 | Koopal Bangestan | P-146 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS-B (2)!F34 | Match
63 | Koopal Bangestan | P-146 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
63 | Koopal Bangestan | P-146 A/B | Currency | EUR | EUR | PUMPS-B (2)!AK27 | Match
63 | Koopal Bangestan | P-146 A/B | Unit Price | 35000 | 35000 | PUMPS-B (2)!AK27 | Match
64 | Koopal Bangestan | P-147 A/B | Equipment Name | Disposal Water Injection Main Pumps | Disposal Water Injection Main Pumps | INS-PUMP-B (1)!AQ31 | Match (INS-PUMP sheet name)
64 | Koopal Bangestan | P-147 A/B | Quantity | 2 | 2 | PUMPS-B (2)!R36 | Match
64 | Koopal Bangestan | P-147 A/B | API 610 Type | BB3 | Centrifugal (BB3) | PUMPS-B (2)!F37 | Match
64 | Koopal Bangestan | P-147 A/B | Pump Family | Centrifugal | Centrifugal (BB3) | PUMPS-B (2)!F37 | Match
64 | Koopal Bangestan | P-147 A/B | Material Class | D-2 | D2 | PUMPS-B (2)!F41 | Match
64 | Koopal Bangestan | P-147 A/B | Capacity (m³/h) | 44 | 44 | PUMPS-B (2)!F38 | Match
64 | Koopal Bangestan | P-147 A/B | Diff. Head (m) | 670 | 670 | PUMPS-B (2)!F39 | Match
64 | Koopal Bangestan | P-147 A/B | Discharge Pressure (barg) | 74.4 | 74.4 | PUMPS-B (2)!F40 | Match
64 | Koopal Bangestan | P-147 A/B | NACE | Y | Y | PUMPS-B (2)!F42 | Match
64 | Koopal Bangestan | P-147 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS-B (2)!F43 | Match
64 | Koopal Bangestan | P-147 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
64 | Koopal Bangestan | P-147 A/B | Currency | EUR | EUR | PUMPS-B (2)!AK36 | Match
64 | Koopal Bangestan | P-147 A/B | Unit Price | 230000 | 230000 | PUMPS-B (2)!AK36 | Match
65 | Koopal Bangestan | P-149 A/B | Equipment Name | Disposal Water Injection Booster Pumps | Disposal Water Injection Booster Pumps | INS-PUMP-B (1)!AQ33 | Match (INS-PUMP sheet name)
65 | Koopal Bangestan | P-149 A/B | Quantity | 2 | 2 | PUMPS-B (3)!R19 | Match
65 | Koopal Bangestan | P-149 A/B | API 610 Type | BB3 | Centrifugal (BB3) | PUMPS-B (3)!F20 | Match
65 | Koopal Bangestan | P-149 A/B | Pump Family | Centrifugal | Centrifugal (BB3) | PUMPS-B (3)!F20 | Match
65 | Koopal Bangestan | P-149 A/B | Material Class | D-2 | D2 | PUMPS-B (3)!F24 | Match
65 | Koopal Bangestan | P-149 A/B | Capacity (m³/h) | 22 | 22 | PUMPS-B (3)!F21 | Match
65 | Koopal Bangestan | P-149 A/B | Diff. Head (m) | 331 | 331 | PUMPS-B (3)!F22 | Match
65 | Koopal Bangestan | P-149 A/B | Discharge Pressure (barg) | 37.4 | 37.4 | PUMPS-B (3)!F23 | Match
65 | Koopal Bangestan | P-149 A/B | NACE | Y | Y | PUMPS-B (3)!F25 | Match
65 | Koopal Bangestan | P-149 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS-B (3)!F26 | Match
65 | Koopal Bangestan | P-149 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
65 | Koopal Bangestan | P-149 A/B | Currency | EUR | EUR | PUMPS-B (3)!AK19 | Match
65 | Koopal Bangestan | P-149 A/B | Unit Price | 160000 | 160000 | PUMPS-B (3)!AK19 | Match
66 | Koopal Bangestan | P-161 A/B | Equipment Name | Dilution Water Pumps | Dilution Water Pumps | PUMPS-B (3)!F28 | Match
66 | Koopal Bangestan | P-161 A/B | Quantity | 2 | 2 | PUMPS-B (3)!R28 | Match
66 | Koopal Bangestan | P-161 A/B | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS-B (3)!F29 | Match
66 | Koopal Bangestan | P-161 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS-B (3)!F29 | Match
66 | Koopal Bangestan | P-161 A/B | Material Class | S-5 | S5 | PUMPS-B (3)!F33 | Match
66 | Koopal Bangestan | P-161 A/B | Capacity (m³/h) | 19 | 19 | PUMPS-B (3)!F30 | Match
66 | Koopal Bangestan | P-161 A/B | Diff. Head (m) | 168 | 168 | PUMPS-B (3)!F31 | Match
66 | Koopal Bangestan | P-161 A/B | Discharge Pressure (barg) | 17.8 | 17.8 | PUMPS-B (3)!F32 | Match
66 | Koopal Bangestan | P-161 A/B | NACE | N | (no NACE line) |  | Inferred – marked
66 | Koopal Bangestan | P-161 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS-B (3)!F34 | Match
66 | Koopal Bangestan | P-161 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
66 | Koopal Bangestan | P-161 A/B | Currency | EUR | EUR | PUMPS-B (3)!AK28 | Match
66 | Koopal Bangestan | P-161 A/B | Unit Price | 16500 | 16500 | PUMPS-B (3)!AK28 | Match
67 | Koopal Bangestan | P-162 | Equipment Name | Dilution Water Pump | Dilution Water Pump | PUMPS-B (3)!F36 | Match
67 | Koopal Bangestan | P-162 | Quantity | 1 | 1 | PUMPS-B (3)!R36 | Match
67 | Koopal Bangestan | P-162 | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS-B (3)!F37 | Match
67 | Koopal Bangestan | P-162 | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS-B (3)!F37 | Match
67 | Koopal Bangestan | P-162 | Material Class | S-5 | S5 | PUMPS-B (3)!F41 | Match
67 | Koopal Bangestan | P-162 | Capacity (m³/h) | 33 | 33 | PUMPS-B (3)!F38 | Match
67 | Koopal Bangestan | P-162 | Diff. Head (m) | 168 | 168 | PUMPS-B (3)!F39 | Match
67 | Koopal Bangestan | P-162 | Discharge Pressure (barg) | 17.8 | 17.8 | PUMPS-B (3)!F40 | Match
67 | Koopal Bangestan | P-162 | NACE | N | (no NACE line) |  | Inferred – marked
67 | Koopal Bangestan | P-162 | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS-B (3)!F42 | Match
67 | Koopal Bangestan | P-162 | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
67 | Koopal Bangestan | P-162 | Currency | EUR | EUR | PUMPS-B (3)!AK36 | Match
67 | Koopal Bangestan | P-162 | Unit Price | 17500 | 17500 | PUMPS-B (3)!AK36 | Match
68 | Koopal Bangestan | P-181 A/B | Equipment Name | Flare K.O. Drum Pumps | Flare K.O. Drum Pumps | PUMPS-B (4)!F19 | Match
68 | Koopal Bangestan | P-181 A/B | Quantity | 2 | 2 | PUMPS-B (4)!R19 | Match
68 | Koopal Bangestan | P-181 A/B | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS-B (4)!F20 | Match
68 | Koopal Bangestan | P-181 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS-B (4)!F20 | Match
68 | Koopal Bangestan | P-181 A/B | Material Class | S-6 | S6 | PUMPS-B (4)!F24 | Match
68 | Koopal Bangestan | P-181 A/B | Capacity (m³/h) | 15 | 15 | PUMPS-B (4)!F21 | Match
68 | Koopal Bangestan | P-181 A/B | Diff. Head (m) | 52 | 52 | PUMPS-B (4)!F22 | Match
68 | Koopal Bangestan | P-181 A/B | Discharge Pressure (barg) | 7.3 | 7.3 | PUMPS-B (4)!F23 | Match
68 | Koopal Bangestan | P-181 A/B | NACE | N | (no NACE line) |  | Inferred – marked
68 | Koopal Bangestan | P-181 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS-B (4)!F25 | Match
68 | Koopal Bangestan | P-181 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
68 | Koopal Bangestan | P-181 A/B | Currency | EUR | EUR | PUMPS-B (4)!AK19 | Match
68 | Koopal Bangestan | P-181 A/B | Unit Price | 10000 | 10000 | PUMPS-B (4)!AK19 | Match
69 | Koopal Bangestan | P-241 A/B | Equipment Name | O.W.S. Oil Pumps | O.W.S. Oil Pumps | PUMPS-B (4)!F27 | Match
69 | Koopal Bangestan | P-241 A/B | Quantity | 2 | 2 | PUMPS-B (4)!R27 | Match
69 | Koopal Bangestan | P-241 A/B | Pump Family | PD-Rotary (Progressing Cavity) | P.D.-Rotary (Progressing Cavity) | PUMPS-B (4)!F28 | Match
69 | Koopal Bangestan | P-241 A/B | Material Class | D-1 | D1 | PUMPS-B (4)!F31 | Match
69 | Koopal Bangestan | P-241 A/B | Capacity (m³/h) | 5.5 | 5.5 | PUMPS-B (4)!F29 | Match
69 | Koopal Bangestan | P-241 A/B | Discharge Pressure (barg) | 3.6 | 3.6 | PUMPS-B (4)!F30 | Match
69 | Koopal Bangestan | P-241 A/B | NACE | Y | Y | PUMPS-B (4)!F32 | Match
69 | Koopal Bangestan | P-241 A/B | Standard / IPS | API 676 + IPS-M-PM-140 | API 676 & IPS-M-PM-140 | PUMPS-B (4)!F33 | Match
69 | Koopal Bangestan | P-241 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
69 | Koopal Bangestan | P-241 A/B | Currency | EUR | EUR | PUMPS-B (4)!AK27 | Match
69 | Koopal Bangestan | P-241 A/B | Unit Price | 25000 | 25000 | PUMPS-B (4)!AK27 | Match
70 | Koopal Bangestan | P-242 A/B | Equipment Name | O.W.S. Water Pumps | O.W.S. Water Pumps | PUMPS-B (4)!F35 | Match
70 | Koopal Bangestan | P-242 A/B | Quantity | 2 | 2 | PUMPS-B (4)!R35 | Match
70 | Koopal Bangestan | P-242 A/B | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS-B (4)!F36 | Match
70 | Koopal Bangestan | P-242 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS-B (4)!F36 | Match
70 | Koopal Bangestan | P-242 A/B | Material Class | D-2 | D2 | PUMPS-B (4)!F40 | Match
70 | Koopal Bangestan | P-242 A/B | Capacity (m³/h) | 11 | 11 | PUMPS-B (4)!F37 | Match
70 | Koopal Bangestan | P-242 A/B | Diff. Head (m) | 28 | 28 | PUMPS-B (4)!F38 | Match
70 | Koopal Bangestan | P-242 A/B | Discharge Pressure (barg) | 3 | 3 | PUMPS-B (4)!F39 | Match
70 | Koopal Bangestan | P-242 A/B | NACE | Y | Y | PUMPS-B (4)!F41 | Match
70 | Koopal Bangestan | P-242 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS-B (4)!F42 | Match
70 | Koopal Bangestan | P-242 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
70 | Koopal Bangestan | P-242 A/B | Currency | EUR | EUR | PUMPS-B (4)!AK35 | Match
70 | Koopal Bangestan | P-242 A/B | Unit Price | 20000 | 20000 | PUMPS-B (4)!AK35 | Match
71 | Koopal Bangestan | P-244 A/B | Equipment Name | Closed Drain Drum Pumps | Closed Drain Drum Pumps | PUMPS-B (5)!F19 | Match
71 | Koopal Bangestan | P-244 A/B | Quantity | 2 | 2 | PUMPS-B (5)!R19 | Match
71 | Koopal Bangestan | P-244 A/B | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS-B (5)!F20 | Match
71 | Koopal Bangestan | P-244 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS-B (5)!F20 | Match
71 | Koopal Bangestan | P-244 A/B | Material Class | D-2 | D2 | PUMPS-B (5)!F24 | Match
71 | Koopal Bangestan | P-244 A/B | Capacity (m³/h) | 15 | 15 | PUMPS-B (5)!F21 | Match
71 | Koopal Bangestan | P-244 A/B | Diff. Head (m) | 61 | 61 | PUMPS-B (5)!F22 | Match
71 | Koopal Bangestan | P-244 A/B | Discharge Pressure (barg) | 9 | 9 | PUMPS-B (5)!F23 | Match
71 | Koopal Bangestan | P-244 A/B | NACE | Y | Y | PUMPS-B (5)!F25 | Match
71 | Koopal Bangestan | P-244 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS-B (5)!F26 | Match
71 | Koopal Bangestan | P-244 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
71 | Koopal Bangestan | P-244 A/B | Currency | EUR | EUR | PUMPS-B (5)!AK19 | Match
71 | Koopal Bangestan | P-244 A/B | Unit Price | 17500 | 17500 | PUMPS-B (5)!AK19 | Match
72 | Koopal Bangestan | P-123 A/B | API 610 Type | OH2 | Centrifugal (OH2) | DESALTERS-B!F33 | Match
72 | Koopal Bangestan | P-123 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | DESALTERS-B!F33 | Match
72 | Koopal Bangestan | P-123 A/B | Material Class | D-2 | D2 | DESALTERS-B!F36 | Match
72 | Koopal Bangestan | P-123 A/B | Capacity (m³/h) | 15 | 15 | DESALTERS-B!F34 | Match
72 | Koopal Bangestan | P-123 A/B | Diff. Head (m) | 44.9 | ΔP 4.4 bar | DESALTERS-B!F35 | Derived – marked
72 | Koopal Bangestan | P-123 A/B | NACE | Y | Y | DESALTERS-B!F37 | Match
72 | Koopal Bangestan | P-123 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | DESALTERS-B!F38 | Match
72 | Koopal Bangestan | P-123 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
72 | Koopal Bangestan | P-123 A/B | Unit Price | (Not stated) | priced inside package | DESALTERS-B | Match
73 | Koopal Bangestan | P-140 A/B | API 610 Type | OH2 | Centrifugal (OH2) | IWWTP-B (1)!F33 | Match
73 | Koopal Bangestan | P-140 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | IWWTP-B (1)!F33 | Match
73 | Koopal Bangestan | P-140 A/B | Material Class | D-2 | D2 | IWWTP-B (1)!F34 | Match
73 | Koopal Bangestan | P-140 A/B | NACE | N | (no NACE line) |  | Inferred – marked
73 | Koopal Bangestan | P-140 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | IWWTP-B (1)!F35 | Match
73 | Koopal Bangestan | P-140 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
73 | Koopal Bangestan | P-140 A/B | Unit Price | (Not stated) | priced inside package | IWWTP-B (1) | Match
74 | Koopal Bangestan | P-141 A/B | API 610 Type | OH2 | Centrifugal (OH2) | IWWTP-B (1)!F38 | Match
74 | Koopal Bangestan | P-141 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | IWWTP-B (1)!F38 | Match
74 | Koopal Bangestan | P-141 A/B | Material Class | D-2 | D2 | IWWTP-B (1)!F39 | Match
74 | Koopal Bangestan | P-141 A/B | NACE | Y | Y | IWWTP-B (1)!F40 | Match
74 | Koopal Bangestan | P-141 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | IWWTP-B (1)!F41 | Match
74 | Koopal Bangestan | P-141 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
74 | Koopal Bangestan | P-141 A/B | Unit Price | (Not stated) | priced inside package | IWWTP-B (1) | Match
75 | Koopal Bangestan | P-142 A/B | API 610 Type | OH2 | Centrifugal (OH2) | IWWTP-B (1)!F38 | Match
75 | Koopal Bangestan | P-142 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | IWWTP-B (1)!F38 | Match
75 | Koopal Bangestan | P-142 A/B | Material Class | D-2 | D2 | IWWTP-B (1)!F39 | Match
75 | Koopal Bangestan | P-142 A/B | NACE | Y | Y | IWWTP-B (1)!F40 | Match
75 | Koopal Bangestan | P-142 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | IWWTP-B (1)!F41 | Match
75 | Koopal Bangestan | P-142 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
75 | Koopal Bangestan | P-142 A/B | Unit Price | (Not stated) | priced inside package | IWWTP-B (1) | Match
76 | Koopal Bangestan | P-143 A/B | Pump Family | PD-Rotary (Gear) | P.D.-Rotary (Ext. Gear) | IWWTP-B (1)!F44 | Match
76 | Koopal Bangestan | P-143 A/B | Material Class | D-1 | D1 | IWWTP-B (1)!F45 | Match
76 | Koopal Bangestan | P-143 A/B | NACE | N | (no NACE line) |  | Inferred – marked
76 | Koopal Bangestan | P-143 A/B | Standard / IPS | API 676 + IPS-M-PM-140 | API 676 & IPS-M-PM-140 | IWWTP-B (1)!F46 | Match
76 | Koopal Bangestan | P-143 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
76 | Koopal Bangestan | P-143 A/B | Unit Price | (Not stated) | priced inside package | IWWTP-B (1) | Match
77 | Koopal Bangestan | P-144 A/B | Pump Family | PD-Rotary (Screw) | P.D.-Rotary (Twin Screw) | IWWTP-B (2)!F17 | Match
77 | Koopal Bangestan | P-144 A/B | Material Class | D-2 | D2 | IWWTP-B (2)!F18 | Match
77 | Koopal Bangestan | P-144 A/B | NACE | Y | Y | IWWTP-B (2)!F19 | Match
77 | Koopal Bangestan | P-144 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | IWWTP-B (2)!F20 | Match
77 | Koopal Bangestan | P-144 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
77 | Koopal Bangestan | P-144 A/B | Unit Price | (Not stated) | priced inside package | IWWTP-B (2) | Match
78 | Koopal Bangestan | P-148 A/B/C | API 610 Type | OH2 | Centrifugal (OH2) | STRIPPER-B!F36 | Match
78 | Koopal Bangestan | P-148 A/B/C | Pump Family | Centrifugal | Centrifugal (OH2) | STRIPPER-B!F36 | Match
78 | Koopal Bangestan | P-148 A/B/C | Material Class | D-2 | D2 | STRIPPER-B!F39 | Match
78 | Koopal Bangestan | P-148 A/B/C | Capacity (m³/h) | 50 | 50 | STRIPPER-B!F37 | Match
78 | Koopal Bangestan | P-148 A/B/C | Diff. Head (m) | 30.6 | ΔP 3.0 bar | STRIPPER-B!F38 | Derived – marked
78 | Koopal Bangestan | P-148 A/B/C | NACE | N | (no NACE line) |  | Inferred – marked
78 | Koopal Bangestan | P-148 A/B/C | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | STRIPPER-B!F40 | Match
78 | Koopal Bangestan | P-148 A/B/C | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
78 | Koopal Bangestan | P-148 A/B/C | Unit Price | (Not stated) | priced inside package | STRIPPER-B | Match
79 | Koopal Asmari | P-153 A/B | Equipment Name | Deaerated Water Pumps | Deaerated Water Pumps | PUMPS-C!F19 | Match
79 | Koopal Asmari | P-153 A/B | Quantity | 2 | 2 | PUMPS-C!R19 | Match
79 | Koopal Asmari | P-153 A/B | Pump Family | Centrifugal | Centrifugal (Horizontal) | PUMPS-C!F20 | Match
79 | Koopal Asmari | P-153 A/B | Material Class | I-2 | I2 | PUMPS-C!F24 | Match
79 | Koopal Asmari | P-153 A/B | Capacity (m³/h) | 48 | 48 | PUMPS-C!F21 | Match
79 | Koopal Asmari | P-153 A/B | Diff. Head (m) | 36 | 36 | PUMPS-C!F22 | Match
79 | Koopal Asmari | P-153 A/B | Discharge Pressure (barg) | 3 | 3 | PUMPS-C!F23 | Match
79 | Koopal Asmari | P-153 A/B | NACE | N | (no NACE line) |  | Inferred – marked
79 | Koopal Asmari | P-153 A/B | Standard / IPS | ISO 5199 + IPS-M-PM-115 | ISO 5199 & IPS-M-PM-115 | PUMPS-C!F25 | Match
79 | Koopal Asmari | P-153 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
79 | Koopal Asmari | P-153 A/B | Currency | EUR | EUR | PUMPS-C!AK19 | Match
79 | Koopal Asmari | P-153 A/B | Unit Price | 6500 | 6500 | PUMPS-C!AK19 | Match
80 | Koopal Asmari | P-158 | Equipment Name | Potable Water Loading Pumps | Potable Water Loading Pump | PUMPS-C!F27 | Match
80 | Koopal Asmari | P-158 | Quantity | 1 | 1 | PUMPS-C!R27 | Match
80 | Koopal Asmari | P-158 | Pump Family | Centrifugal | Centrifugal (Horizontal) | PUMPS-C!F28 | Match
80 | Koopal Asmari | P-158 | Material Class | I-2 | I2 | PUMPS-C!F32 | Match
80 | Koopal Asmari | P-158 | Capacity (m³/h) | 33 | 33 | PUMPS-C!F29 | Match
80 | Koopal Asmari | P-158 | Diff. Head (m) | 31 | 31 | PUMPS-C!F30 | Match
80 | Koopal Asmari | P-158 | Discharge Pressure (barg) | 2.9 | 2.9 | PUMPS-C!F31 | Match
80 | Koopal Asmari | P-158 | NACE | N | (no NACE line) |  | Inferred – marked
80 | Koopal Asmari | P-158 | Standard / IPS | ISO 5199 + IPS-M-PM-115 | ISO 5199 & IPS-M-PM-115 | PUMPS-C!F33 | Match
80 | Koopal Asmari | P-158 | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
80 | Koopal Asmari | P-158 | Currency | EUR | EUR | PUMPS-C!AK27 | Match
80 | Koopal Asmari | P-158 | Unit Price | 6500 | 6500 | PUMPS-C!AK27 | Match
81 | Koopal Asmari | P-172 | Equipment Name | Flare K.O. Drums Sump Pump | Flare K.O. Drums Sump Pump | PUMPS-C!F35 | Match
81 | Koopal Asmari | P-172 | Quantity | 1 | 1 | PUMPS-C!R35 | Match
81 | Koopal Asmari | P-172 | API 610 Type | VS4 | Centrifugal (VS4) | PUMPS-C!F36 | Match
81 | Koopal Asmari | P-172 | Pump Family | Centrifugal | Centrifugal (VS4) | PUMPS-C!F36 | Match
81 | Koopal Asmari | P-172 | Material Class | S-6 | S6 | PUMPS-C!F40 | Match
81 | Koopal Asmari | P-172 | Capacity (m³/h) | 5.5 | 5.5 | PUMPS-C!F37 | Match
81 | Koopal Asmari | P-172 | Diff. Head (m) | 43 | 43 | PUMPS-C!F38 | Match
81 | Koopal Asmari | P-172 | Discharge Pressure (barg) | 3.03 | 3.03 | PUMPS-C!F39 | Match
81 | Koopal Asmari | P-172 | NACE | N | (no NACE line) |  | Inferred – marked
81 | Koopal Asmari | P-172 | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS-C!F41 | Match
81 | Koopal Asmari | P-172 | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
81 | Koopal Asmari | P-172 | Currency | EUR | EUR | PUMPS-C!AK35 | Match
81 | Koopal Asmari | P-172 | Unit Price | 10000 | 10000 | PUMPS-C!AK35 | Match
82 | Koopal Asmari | P-201 | Equipment Name | Fuel Oil Pump | Fuel Oil Pump | PUMPS-C!F43 | Match
82 | Koopal Asmari | P-201 | Quantity | 1 | 1 | PUMPS-C!R43 | Match
82 | Koopal Asmari | P-201 | Pump Family | Centrifugal | Centrifugal (Horizontal) | PUMPS-C!F44 | Match
82 | Koopal Asmari | P-201 | Material Class | S-1 | S1 | PUMPS-C!F48 | Match
82 | Koopal Asmari | P-201 | Capacity (m³/h) | 10 | 10 | PUMPS-C!F45 | Match
82 | Koopal Asmari | P-201 | Diff. Head (m) | 41 | 41 | PUMPS-C!F46 | Match
82 | Koopal Asmari | P-201 | Discharge Pressure (barg) | 3.1 | 3.1 | PUMPS-C!F47 | Match
82 | Koopal Asmari | P-201 | NACE | N | (no NACE line) |  | Inferred – marked
82 | Koopal Asmari | P-201 | Standard / IPS | ISO 5199 + IPS-M-PM-115 | ISO 5199 & IPS-M-PM-115 | PUMPS-C!F49 | Match
82 | Koopal Asmari | P-201 | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
82 | Koopal Asmari | P-201 | Currency | EUR | EUR | PUMPS-C!AK43 | Match
82 | Koopal Asmari | P-201 | Unit Price | 7000 | 7000 | PUMPS-C!AK43 | Match
83 | Koopal Asmari | P-235 | Equipment Name | Closed Drain Drums Sump Pump | Closed Drain Drums Sump Pump | PUMPS-C (2)!F19 | Match
83 | Koopal Asmari | P-235 | Quantity | 1 | 1 | PUMPS-C (2)!R19 | Match
83 | Koopal Asmari | P-235 | API 610 Type | VS4 | Centrifugal (VS4) | PUMPS-C (2)!F20 | Match
83 | Koopal Asmari | P-235 | Pump Family | Centrifugal | Centrifugal (VS4) | PUMPS-C (2)!F20 | Match
83 | Koopal Asmari | P-235 | Material Class | S-6 | S6 | PUMPS-C (2)!F24 | Match
83 | Koopal Asmari | P-235 | Capacity (m³/h) | 5.5 | 5.5 | PUMPS-C (2)!F21 | Match
83 | Koopal Asmari | P-235 | Diff. Head (m) | 31 | 31 | PUMPS-C (2)!F22 | Match
83 | Koopal Asmari | P-235 | Discharge Pressure (barg) | 3.4 | 3.4 | PUMPS-C (2)!F23 | Match
83 | Koopal Asmari | P-235 | NACE | N | (no NACE line) |  | Inferred – marked
83 | Koopal Asmari | P-235 | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS-C (2)!F25 | Match
83 | Koopal Asmari | P-235 | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
83 | Koopal Asmari | P-235 | Currency | EUR | EUR | PUMPS-C (2)!AK19 | Match
83 | Koopal Asmari | P-235 | Unit Price | 10000 | 10000 | PUMPS-C (2)!AK19 | Match
84 | Koopal Asmari | P-270 | Equipment Name | Fire Water Pump-Elect. Motor Driven | Fire Water Pump-Elect. Motor Driven | PUMPS-C (2)!F27 | Match
84 | Koopal Asmari | P-270 | Quantity | 1 | 1 | PUMPS-C (2)!R27 | Match
84 | Koopal Asmari | P-270 | API 610 Type | BB (unspecified) | Centrifugal (Horizontal, Impeller Between Bearings Design) | PUMPS-C (2)!F28 | Match
84 | Koopal Asmari | P-270 | Pump Family | Centrifugal | Centrifugal (Horizontal, Impeller Between Bearings Design) | PUMPS-C (2)!F28 | Match
84 | Koopal Asmari | P-270 | Material Class | I-2 | I2 | PUMPS-C (2)!F33 | Match
84 | Koopal Asmari | P-270 | Capacity (m³/h) | 770 | 770 | PUMPS-C (2)!F30 | Match
84 | Koopal Asmari | P-270 | Diff. Head (m) | 107 | 107 | PUMPS-C (2)!F31 | Match
84 | Koopal Asmari | P-270 | Discharge Pressure (barg) | 11.3 | 11.3 | PUMPS-C (2)!F32 | Match
84 | Koopal Asmari | P-270 | NACE | N | (no NACE line) |  | Inferred – marked
84 | Koopal Asmari | P-270 | Standard / IPS | NFPA 20 + IPS-M-PM-125 | NFPA 20 & IPS-M-PM-125 | PUMPS-C (2)!F34 | Match
84 | Koopal Asmari | P-270 | Driver Type | Electric Motor | name: electric | Equipment Name | Match
84 | Koopal Asmari | P-270 | Currency | EUR | EUR | PUMPS-C (2)!AK27 | Match
84 | Koopal Asmari | P-270 | Unit Price | 70000 | 70000 | PUMPS-C (2)!AK27 | Match
85 | Koopal Asmari | P-271 | Equipment Name | Fire Water Pump-Diesel Engine Driven | Fire Water Pump-Diesel Engine Driven | PUMPS-C (2)!F36 | Match
85 | Koopal Asmari | P-271 | Quantity | 1 | 1 | PUMPS-C (2)!R36 | Match
85 | Koopal Asmari | P-271 | API 610 Type | BB (unspecified) | Centrifugal (Horizontal, Impeller Between Bearings Design) | PUMPS-C (2)!F37 | Match
85 | Koopal Asmari | P-271 | Pump Family | Centrifugal | Centrifugal (Horizontal, Impeller Between Bearings Design) | PUMPS-C (2)!F37 | Match
85 | Koopal Asmari | P-271 | Material Class | I-2 | I2 | PUMPS-C (2)!F42 | Match
85 | Koopal Asmari | P-271 | Capacity (m³/h) | 770 | 770 | PUMPS-C (2)!F39 | Match
85 | Koopal Asmari | P-271 | Diff. Head (m) | 88.7 | 88.7 | PUMPS-C (2)!F40 | Match
85 | Koopal Asmari | P-271 | Discharge Pressure (barg) | 9.5 | 9.5 | PUMPS-C (2)!F41 | Match
85 | Koopal Asmari | P-271 | NACE | N | (no NACE line) |  | Inferred – marked
85 | Koopal Asmari | P-271 | Standard / IPS | NFPA 20 + IPS-M-PM-125 | NFPA 20 & IPS-M-PM-125 | PUMPS-C (2)!F43 | Match
85 | Koopal Asmari | P-271 | Driver Type | Diesel Engine | name: diesel | Equipment Name | Match
85 | Koopal Asmari | P-271 | Currency | EUR | EUR | PUMPS-C (2)!AK36 | Match
85 | Koopal Asmari | P-271 | Unit Price | 90000 | 90000 | PUMPS-C (2)!AK36 | Match
86 | Koopal Asmari | P-272 A/B | Equipment Name | Fire Water Jockey Pumps | Fire Water Jockey Pumps | PUMPS-C (3)!F19 | Match
86 | Koopal Asmari | P-272 A/B | Quantity | 2 | 2 | PUMPS-C (3)!R19 | Match
86 | Koopal Asmari | P-272 A/B | API 610 Type | OH (unspecified) | Centrifugal (Horizontal, Overhung Impeller Design) | PUMPS-C (3)!F20 | Match
86 | Koopal Asmari | P-272 A/B | Pump Family | Centrifugal | Centrifugal (Horizontal, Overhung Impeller Design) | PUMPS-C (3)!F20 | Match
86 | Koopal Asmari | P-272 A/B | Material Class | I-2 | I2 | PUMPS-C (3)!F25 | Match
86 | Koopal Asmari | P-272 A/B | Capacity (m³/h) | 16.5 | 16.5 | PUMPS-C (3)!F22 | Match
86 | Koopal Asmari | P-272 A/B | Diff. Head (m) | 107 | 107 | PUMPS-C (3)!F23 | Match
86 | Koopal Asmari | P-272 A/B | Discharge Pressure (barg) | 11.3 | 11.3 | PUMPS-C (3)!F24 | Match
86 | Koopal Asmari | P-272 A/B | NACE | N | (no NACE line) |  | Inferred – marked
86 | Koopal Asmari | P-272 A/B | Standard / IPS | NFPA 20 + IPS-M-PM-125 | NFPA 20 & IPS-M-PM-125 | PUMPS-C (3)!F26 | Match
86 | Koopal Asmari | P-272 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
86 | Koopal Asmari | P-272 A/B | Currency | EUR | EUR | PUMPS-C (3)!AK19 | Match
86 | Koopal Asmari | P-272 A/B | Unit Price | 15000 | 15000 | PUMPS-C (3)!AK19 | Match
87 | Koopal Asmari | P-273 | Equipment Name | Fire Water Loading Pump | Fire Water Loading Pump | PUMPS-C (3)!F28 | Match
87 | Koopal Asmari | P-273 | Quantity | 1 | 1 | PUMPS-C (3)!R28 | Match
87 | Koopal Asmari | P-273 | Pump Family | Centrifugal | Centrifugal (Horizontal) | PUMPS-C (3)!F29 | Match
87 | Koopal Asmari | P-273 | Material Class | I-2 | I2 | PUMPS-C (3)!F33 | Match
87 | Koopal Asmari | P-273 | Capacity (m³/h) | 33 | 33 | PUMPS-C (3)!F30 | Match
87 | Koopal Asmari | P-273 | Diff. Head (m) | 30.6 | 30.6 | PUMPS-C (3)!F31 | Match
87 | Koopal Asmari | P-273 | Discharge Pressure (barg) | 2.9 | 2.9 | PUMPS-C (3)!F32 | Match
87 | Koopal Asmari | P-273 | NACE | N | (no NACE line) |  | Inferred – marked
87 | Koopal Asmari | P-273 | Standard / IPS | ISO 5199 + IPS-M-PM-115 | ISO 5199 & IPS-M-PM-115 | PUMPS-C (3)!F34 | Match
87 | Koopal Asmari | P-273 | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
87 | Koopal Asmari | P-273 | Currency | EUR | EUR | PUMPS-C (3)!AK28 | Match
87 | Koopal Asmari | P-273 | Unit Price | 6500 | 6500 | PUMPS-C (3)!AK28 | Match
88 | Koopal Asmari | P-154 A/B | Equipment Name | Cooling Water (Sealing System) Recycle Pumps | Cooling Water (Sealing System) Recycle Pumps | PUMPS-C (3)!F41 | Match
88 | Koopal Asmari | P-154 A/B | Quantity | 2 | 2 | PUMPS-C (3)!R41 | Match
88 | Koopal Asmari | P-154 A/B | Pump Family | Centrifugal | Centrifugal (Horizontal) | PUMPS-C (3)!F44 | Match
88 | Koopal Asmari | P-154 A/B | Material Class | I-2 | I2 | PUMPS-C (3)!F47 | Match
88 | Koopal Asmari | P-154 A/B | Capacity (m³/h) | 3 | 3 | PUMPS-C (3)!F45 | Match
88 | Koopal Asmari | P-154 A/B | Diff. Head (m) | 30.6 | ΔP 3.0 bar | PUMPS-C (3)!F46 | Derived – marked
88 | Koopal Asmari | P-154 A/B | NACE | N | (no NACE line) |  | Inferred – marked
88 | Koopal Asmari | P-154 A/B | Standard / IPS | ISO 5199 + IPS-M-PM-115 | ISO 5199 & IPS-M-PM-115 | PUMPS-C (3)!F48 | Match
88 | Koopal Asmari | P-154 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
88 | Koopal Asmari | P-154 A/B | Currency | IRR | IRR | PUMPS-C (3)!U41 | Match
88 | Koopal Asmari | P-154 A/B | Unit Price | 300000000 | 300000000 | PUMPS-C (3)!U41 | Match
89 | Koopal Asmari | P-157 A/B | Equipment Name | Water Liquid Return Pumps (Deaeration System) | Water Liquid Return Pumps | PUMPS-C (4)!F19 | Match
89 | Koopal Asmari | P-157 A/B | Quantity | 2 | 2 | PUMPS-C (4)!R19 | Match
89 | Koopal Asmari | P-157 A/B | Pump Family | Centrifugal | Centrifugal (Horizontal) | PUMPS-C (4)!F21 | Match
89 | Koopal Asmari | P-157 A/B | Material Class | I-2 | I2 | PUMPS-C (4)!F24 | Match
89 | Koopal Asmari | P-157 A/B | Capacity (m³/h) | 2 | 2 | PUMPS-C (4)!F22 | Match
89 | Koopal Asmari | P-157 A/B | Diff. Head (m) | 30.6 | ΔP 3.0 bar | PUMPS-C (4)!F23 | Derived – marked
89 | Koopal Asmari | P-157 A/B | NACE | N | (no NACE line) |  | Inferred – marked
89 | Koopal Asmari | P-157 A/B | Standard / IPS | ISO 5199 + IPS-M-PM-115 | ISO 5199 & IPS-M-PM-115 | PUMPS-C (4)!F25 | Match
89 | Koopal Asmari | P-157 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
89 | Koopal Asmari | P-157 A/B | Currency | IRR | IRR | PUMPS-C (4)!U19 | Match
89 | Koopal Asmari | P-157 A/B | Unit Price | 250000000 | 250000000 | PUMPS-C (4)!U19 | Match
90 | Koopal Asmari | P-236 | Equipment Name | Evaporation Pond Portable Pump | Evaporation Pond Portable Pump | PUMPS-A (4)!F19 | Match
90 | Koopal Asmari | P-236 | Quantity | 1 | 1 | PUMPS-A (4)!R19 | Match
90 | Koopal Asmari | P-236 | Pump Family | Centrifugal - Submersible | Centrifugal , Submersible | PUMPS-A (4)!F20 | Match
90 | Koopal Asmari | P-236 | Material Class | D-2 | D2 | PUMPS-A (4)!F25 | Match
90 | Koopal Asmari | P-236 | Capacity (m³/h) | 6 | 6 | PUMPS-A (4)!F23 | Match
90 | Koopal Asmari | P-236 | Diff. Head (m) | 20.4 | ΔP 2.0 bar | PUMPS-A (4)!F24 | Derived – marked
90 | Koopal Asmari | P-236 | NACE | N | (no NACE line) |  | Inferred – marked
90 | Koopal Asmari | P-236 | Standard / IPS | JIS B 8325 + None | JIS B 8325 | PUMPS-A (4)!F26 | Match
90 | Koopal Asmari | P-236 | Driver Type | Electric Motor | Electric Motor | PUMPS-A (4)!F21 | Match
90 | Koopal Asmari | P-236 | Currency | EUR | EUR | PUMPS-A (4)!AK19 | Match
90 | Koopal Asmari | P-236 | Unit Price | 20000 | 20000 | PUMPS-A (4)!AK19 | Match
91 | Koopal Bangestan | P-246 | Equipment Name | Evaporation Pond Portable Pump | Evaporation Pond Portable Pump | PUMPS-B (5)!F28 | Match
91 | Koopal Bangestan | P-246 | Quantity | 1 | 1 | PUMPS-B (5)!R28 | Match
91 | Koopal Bangestan | P-246 | Pump Family | Centrifugal - Submersible | Centrifugal , Submersible | PUMPS-B (5)!F29 | Match
91 | Koopal Bangestan | P-246 | Material Class | D-2 | D2 | PUMPS-B (5)!F34 | Match
91 | Koopal Bangestan | P-246 | Capacity (m³/h) | 6 | 6 | PUMPS-B (5)!F32 | Match
91 | Koopal Bangestan | P-246 | Diff. Head (m) | 20.4 | ΔP 2.0 bar | PUMPS-B (5)!F33 | Derived – marked
91 | Koopal Bangestan | P-246 | NACE | N | (no NACE line) |  | Inferred – marked
91 | Koopal Bangestan | P-246 | Standard / IPS | JIS B 8325 + None | JIS B 8325 | PUMPS-B (5)!F35 | Match
91 | Koopal Bangestan | P-246 | Driver Type | Electric Motor | Electric Motor | PUMPS-B (5)!F30 | Match
91 | Koopal Bangestan | P-246 | Currency | EUR | EUR | PUMPS-B (5)!AK28 | Match
91 | Koopal Bangestan | P-246 | Unit Price | 20000 | 20000 | PUMPS-B (5)!AK28 | Match
92 | Koopal Asmari | P-220 A/B/C/D/E | Equipment Name | Chemical Loading Pumps | Chemical Loading Pumps | PUMPS-C (3)!F36 | Match
92 | Koopal Asmari | P-220 A/B/C/D/E | Quantity | 5 | 5 | PUMPS-C (3)!R36 | Match
92 | Koopal Asmari | P-220 A/B/C/D/E | Pump Family | Portable Barrel | Portable Barrel Pump | PUMPS-C (3)!F37 | Match
92 | Koopal Asmari | P-220 A/B/C/D/E | Material Class | SS316L (non-API) | S.S. 316 L | PUMPS-C (3)!F40 | Match
92 | Koopal Asmari | P-220 A/B/C/D/E | Capacity (m³/h) | 9.6 | 9.6 | PUMPS-C (3)!F38 (L/min→m³/h) | Match
92 | Koopal Asmari | P-220 A/B/C/D/E | NACE | N | (no NACE line) |  | Inferred – marked
92 | Koopal Asmari | P-220 A/B/C/D/E | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
92 | Koopal Asmari | P-220 A/B/C/D/E | Currency | IRR | IRR | PUMPS-C (3)!U36 | Match
92 | Koopal Asmari | P-220 A/B/C/D/E | Unit Price | 100000000 | 100000000 | PUMPS-C (3)!U36 | Match
93 | Koopal Asmari | P-116 | Equipment Name | Water Glycol Loading Pump | Water Glycol Loading Pump | PUMPS-C (4)!F27 | Match
93 | Koopal Asmari | P-116 | Quantity | 1 | 1 | PUMPS-C (4)!R27 | Match
93 | Koopal Asmari | P-116 | Pump Family | Portable Barrel | Portable Barrel Pump | PUMPS-C (4)!F28 | Match
93 | Koopal Asmari | P-116 | Material Class | SS316L (non-API) | S.S. 316 L | PUMPS-C (4)!F31 | Match
93 | Koopal Asmari | P-116 | Capacity (m³/h) | 9.6 | 9.6 | PUMPS-C (4)!F29 | Match
93 | Koopal Asmari | P-116 | NACE | N | (no NACE line) |  | Inferred – marked
93 | Koopal Asmari | P-116 | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
93 | Koopal Asmari | P-116 | Currency | IRR | IRR | PUMPS-C (4)!U27 | Match
93 | Koopal Asmari | P-116 | Unit Price | 100000000 | 100000000 | PUMPS-C (4)!U27 | Match
94 | Pazanan 2 | P-111 A/B | Equipment Name | Off Spec. Crude Pumps | Off Spec. Crude Pumps | PUMPS!B8 | Match
94 | Pazanan 2 | P-111 A/B | Quantity | 2 | 2 | PUMPS!C8 | Match
94 | Pazanan 2 | P-111 A/B | API 610 Type | VS6 | Centrifugal (VS6) | PUMPS!B8 | Match
94 | Pazanan 2 | P-111 A/B | Pump Family | Centrifugal | Centrifugal (VS6) | PUMPS!B8 | Match
94 | Pazanan 2 | P-111 A/B | Material Class | D-1 | D1 | PUMPS!B8 | Match
94 | Pazanan 2 | P-111 A/B | Capacity (m³/h) | 45 | 45 | PUMPS!B8 | Match
94 | Pazanan 2 | P-111 A/B | Diff. Head (m) | 139.1 | 139.1 | PUMPS!B8 | Match
94 | Pazanan 2 | P-111 A/B | Discharge Pressure (barg) | 14.5 | 14.5 | PUMPS!B8 | Match
94 | Pazanan 2 | P-111 A/B | NACE | Y | Y | PUMPS!B8 | Match
94 | Pazanan 2 | P-111 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS!B8 | Match
94 | Pazanan 2 | P-111 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
94 | Pazanan 2 | P-111 A/B | Currency | EUR | EUR | PUMPS!F8 | Match
94 | Pazanan 2 | P-111 A/B | Unit Price | 111500 | 111500 | PUMPS!F8 | Match
95 | Pazanan 2 | P-122 A/B | Equipment Name | Deaerated Water Pumps | Deaerated Water Pumps | PUMPS!B9 | Match
95 | Pazanan 2 | P-122 A/B | Quantity | 2 | 2 | PUMPS!C9 | Match
95 | Pazanan 2 | P-122 A/B | Pump Family | Centrifugal | Centrifugal (Horizontal) | PUMPS!B9 | Match
95 | Pazanan 2 | P-122 A/B | Material Class | I-2 | I2 | PUMPS!B9 | Match
95 | Pazanan 2 | P-122 A/B | Capacity (m³/h) | 53 | 53 | PUMPS!B9 | Match
95 | Pazanan 2 | P-122 A/B | Diff. Head (m) | 35.7 | 35.7 | PUMPS!B9 | Match
95 | Pazanan 2 | P-122 A/B | Discharge Pressure (barg) | 2.9 | 2.9 | PUMPS!B9 | Match
95 | Pazanan 2 | P-122 A/B | NACE | N | (no NACE line) |  | Inferred – marked
95 | Pazanan 2 | P-122 A/B | Standard / IPS | ISO 5199 + IPS-M-PM-115 | ISO 5199 & IPS-M-PM-115 | PUMPS!B9 | Match
95 | Pazanan 2 | P-122 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
95 | Pazanan 2 | P-122 A/B | Currency | EUR | EUR | PUMPS!F9 | Match
95 | Pazanan 2 | P-122 A/B | Unit Price | 15050 | 15050 | PUMPS!F9 | Match
96 | Pazanan 2 | P-124 | Equipment Name | Dilution Water Pump | Dilution Water Pump | PUMPS!B10 | Match
96 | Pazanan 2 | P-124 | Quantity | 1 | 1 | PUMPS!C10 | Match
96 | Pazanan 2 | P-124 | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS!B10 | Match
96 | Pazanan 2 | P-124 | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS!B10 | Match
96 | Pazanan 2 | P-124 | Material Class | I-2 | I2 | PUMPS!B10 | Match
96 | Pazanan 2 | P-124 | Capacity (m³/h) | 53 | 53 | PUMPS!B10 | Match
96 | Pazanan 2 | P-124 | Diff. Head (m) | 122.3 | 122.3 | PUMPS!B10 | Match
96 | Pazanan 2 | P-124 | Discharge Pressure (barg) | 12 | 12 | PUMPS!B10 | Match
96 | Pazanan 2 | P-124 | NACE | N | (no NACE line) |  | Inferred – marked
96 | Pazanan 2 | P-124 | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS!B10 | Match
96 | Pazanan 2 | P-124 | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
96 | Pazanan 2 | P-124 | Currency | EUR | EUR | PUMPS!F10 | Match
96 | Pazanan 2 | P-124 | Unit Price | 22250 | 22250 | PUMPS!F10 | Match
97 | Pazanan 2 | P-125 A/B | Equipment Name | Dilution Water Pumps | Dilution Water Pumps | PUMPS!B11 | Match
97 | Pazanan 2 | P-125 A/B | Quantity | 2 | 2 | PUMPS!C11 | Match
97 | Pazanan 2 | P-125 A/B | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS!B11 | Match
97 | Pazanan 2 | P-125 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS!B11 | Match
97 | Pazanan 2 | P-125 A/B | Material Class | I-2 | I2 | PUMPS!B11 | Match
97 | Pazanan 2 | P-125 A/B | Capacity (m³/h) | 31 | 31 | PUMPS!B11 | Match
97 | Pazanan 2 | P-125 A/B | Diff. Head (m) | 122 | 122 | PUMPS!B11 | Match
97 | Pazanan 2 | P-125 A/B | Discharge Pressure (barg) | 13 | 13 | PUMPS!B11 | Match
97 | Pazanan 2 | P-125 A/B | NACE | N | (no NACE line) |  | Inferred – marked
97 | Pazanan 2 | P-125 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS!B11 | Match
97 | Pazanan 2 | P-125 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
97 | Pazanan 2 | P-125 A/B | Currency | EUR | EUR | PUMPS!F11 | Match
97 | Pazanan 2 | P-125 A/B | Unit Price | 21500 | 21500 | PUMPS!F11 | Match
98 | Pazanan 2 | P-136 A/B | Equipment Name | Disposal Water InjectionPumps | Disposal Water InjectionPumps | PUMPS!B12 | Match
98 | Pazanan 2 | P-136 A/B | Quantity | 2 | 2 | PUMPS!C12 | Match
98 | Pazanan 2 | P-136 A/B | API 610 Type | BB3 | Centrifugal (BB3) | PUMPS!B12 | Match
98 | Pazanan 2 | P-136 A/B | Pump Family | Centrifugal | Centrifugal (BB3) | PUMPS!B12 | Match
98 | Pazanan 2 | P-136 A/B | Material Class | D-2 | D2 | PUMPS!B12 | Match
98 | Pazanan 2 | P-136 A/B | Capacity (m³/h) | 91 | 91 | PUMPS!B12 | Match
98 | Pazanan 2 | P-136 A/B | Diff. Head (m) | 650 | 650 | PUMPS!B12 | Match
98 | Pazanan 2 | P-136 A/B | Discharge Pressure (barg) | 72.8 | 72.8 | PUMPS!B12 | Match
98 | Pazanan 2 | P-136 A/B | NACE | Y | Y | PUMPS!B12 | Match
98 | Pazanan 2 | P-136 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS!B12 | Match
98 | Pazanan 2 | P-136 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
98 | Pazanan 2 | P-136 A/B | Currency | EUR | EUR | PUMPS!F12 | Match
98 | Pazanan 2 | P-136 A/B | Unit Price | 317500 | 317500 | PUMPS!F12 | Match
99 | Pazanan 2 | P-137 A/B | Equipment Name | Dirty Oil Pumps | Dirty Oil Pumps | PUMPS!B13 | Match
99 | Pazanan 2 | P-137 A/B | Quantity | 2 | 2 | PUMPS!C13 | Match
99 | Pazanan 2 | P-137 A/B | Pump Family | PD-Rotary (Gear) | P.D.-Rotary (Ext. Gear) | PUMPS!B13 | Match
99 | Pazanan 2 | P-137 A/B | Material Class | D-1 | D1 | PUMPS!B13 | Match
99 | Pazanan 2 | P-137 A/B | Capacity (m³/h) | 5 | 5 | PUMPS!B13 | Match
99 | Pazanan 2 | P-137 A/B | Discharge Pressure (barg) | 8 | 8 | PUMPS!B13 | Match
99 | Pazanan 2 | P-137 A/B | NACE | Y | Y | PUMPS!B13 | Match
99 | Pazanan 2 | P-137 A/B | Standard / IPS | API 676 + IPS-M-PM-140 | API 676 & IPS-M-PM-140 | PUMPS!B13 | Match
99 | Pazanan 2 | P-137 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
99 | Pazanan 2 | P-137 A/B | Currency | EUR | EUR | PUMPS!F13 | Match
99 | Pazanan 2 | P-137 A/B | Unit Price | 30000 | 30000 | PUMPS!F13 | Match
100 | Pazanan 2 | P-138 A/B | Equipment Name | Evaporation Pond Water Return Pumps | Evaporation Pond Water Return Pumps | PUMPS!B14 | Match
100 | Pazanan 2 | P-138 A/B | Quantity | 2 | 2 | PUMPS!C14 | Match
100 | Pazanan 2 | P-138 A/B | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS!B14 | Match
100 | Pazanan 2 | P-138 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS!B14 | Match
100 | Pazanan 2 | P-138 A/B | Material Class | D-2 | D2 | PUMPS!B14 | Match
100 | Pazanan 2 | P-138 A/B | Capacity (m³/h) | 15 | 15 | PUMPS!B14 | Match
100 | Pazanan 2 | P-138 A/B | Diff. Head (m) | 27 | 27 | PUMPS!B14 | Match
100 | Pazanan 2 | P-138 A/B | Discharge Pressure (barg) | 3.2 | 3.2 | PUMPS!B14 | Match
100 | Pazanan 2 | P-138 A/B | NACE | N | (no NACE line) |  | Inferred – marked
100 | Pazanan 2 | P-138 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS!B14 | Match
100 | Pazanan 2 | P-138 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
100 | Pazanan 2 | P-138 A/B | Currency | EUR | EUR | PUMPS!F14 | Match
100 | Pazanan 2 | P-138 A/B | Unit Price | 29000 | 29000 | PUMPS!F14 | Match
101 | Pazanan 2 | P-139 A/B/C | Equipment Name | Disposal Water InjectionPumps | Disposal Water InjectionPumps | PUMPS!B15 | Match
101 | Pazanan 2 | P-139 A/B/C | Quantity | 3 | 3 | PUMPS!C15 | Match
101 | Pazanan 2 | P-139 A/B/C | API 610 Type | BB3 | Centrifugal (BB3) | PUMPS!B15 | Match
101 | Pazanan 2 | P-139 A/B/C | Pump Family | Centrifugal | Centrifugal (BB3) | PUMPS!B15 | Match
101 | Pazanan 2 | P-139 A/B/C | Material Class | D-2 | D2 | PUMPS!B15 | Match
101 | Pazanan 2 | P-139 A/B/C | Capacity (m³/h) | 44 | 44 | PUMPS!B15 | Match
101 | Pazanan 2 | P-139 A/B/C | Diff. Head (m) | 385 | 385 | PUMPS!B15 | Match
101 | Pazanan 2 | P-139 A/B/C | Discharge Pressure (barg) | 48.2 | 48.2 | PUMPS!B15 | Match
101 | Pazanan 2 | P-139 A/B/C | NACE | Y | Y | PUMPS!B15 | Match
101 | Pazanan 2 | P-139 A/B/C | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS!B15 | Match
101 | Pazanan 2 | P-139 A/B/C | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
101 | Pazanan 2 | P-139 A/B/C | Currency | EUR | EUR | PUMPS!F15 | Match
101 | Pazanan 2 | P-139 A/B/C | Unit Price | 247500 | 247500 | PUMPS!F15 | Match
102 | Pazanan 2 | P-151 A/B | Equipment Name | Flare K.O. Drum Pumps | Flare K.O. Drum Pumps | PUMPS!B16 | Match
102 | Pazanan 2 | P-151 A/B | Quantity | 2 | 2 | PUMPS!C16 | Match
102 | Pazanan 2 | P-151 A/B | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS!B16 | Match
102 | Pazanan 2 | P-151 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS!B16 | Match
102 | Pazanan 2 | P-151 A/B | Material Class | S-6 | S6 | PUMPS!B16 | Match
102 | Pazanan 2 | P-151 A/B | Capacity (m³/h) | 10 | 10 | PUMPS!B16 | Match
102 | Pazanan 2 | P-151 A/B | Diff. Head (m) | 40 | 40 | PUMPS!B16 | Match
102 | Pazanan 2 | P-151 A/B | Discharge Pressure (barg) | 6.8 | 6.8 | PUMPS!B16 | Match
102 | Pazanan 2 | P-151 A/B | NACE | N | (no NACE line) |  | Inferred – marked
102 | Pazanan 2 | P-151 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS!B16 | Match
102 | Pazanan 2 | P-151 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
102 | Pazanan 2 | P-151 A/B | Currency | EUR | EUR | PUMPS!F16 | Match
102 | Pazanan 2 | P-151 A/B | Unit Price | 25500 | 25500 | PUMPS!F16 | Match
103 | Pazanan 2 | P-161 A/B | Equipment Name | Closed Drain Drum Pumps | Closed Drain Drum Pumps | PUMPS!B17 | Match
103 | Pazanan 2 | P-161 A/B | Quantity | 2 | 2 | PUMPS!C17 | Match
103 | Pazanan 2 | P-161 A/B | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS!B17 | Match
103 | Pazanan 2 | P-161 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS!B17 | Match
103 | Pazanan 2 | P-161 A/B | Material Class | D-2 | D2 | PUMPS!B17 | Match
103 | Pazanan 2 | P-161 A/B | Capacity (m³/h) | 25 | 25 | PUMPS!B17 | Match
103 | Pazanan 2 | P-161 A/B | Diff. Head (m) | 55 | 55 | PUMPS!B17 | Match
103 | Pazanan 2 | P-161 A/B | Discharge Pressure (barg) | 5 | 5 | PUMPS!B17 | Match
103 | Pazanan 2 | P-161 A/B | NACE | Y | Y | PUMPS!B17 | Match
103 | Pazanan 2 | P-161 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS!B17 | Match
103 | Pazanan 2 | P-161 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
103 | Pazanan 2 | P-161 A/B | Currency | EUR | EUR | PUMPS!F17 | Match
103 | Pazanan 2 | P-161 A/B | Unit Price | 31000 | 31000 | PUMPS!F17 | Match
104 | Pazanan 2 | P-162 | Equipment Name | C. D. Drum / Flare K.O. Drum Sump Pump | C. D. Drum / Flare K.O. Drum Sump Pump | PUMPS!B18 | Match
104 | Pazanan 2 | P-162 | Quantity | 1 | 1 | PUMPS!C18 | Match
104 | Pazanan 2 | P-162 | API 610 Type | VS4 | Centrifugal (VS4) | PUMPS!B18 | Match
104 | Pazanan 2 | P-162 | Pump Family | Centrifugal | Centrifugal (VS4) | PUMPS!B18 | Match
104 | Pazanan 2 | P-162 | Material Class | S-6 | S6 | PUMPS!B18 | Match
104 | Pazanan 2 | P-162 | Capacity (m³/h) | 5 | 5 | PUMPS!B18 | Match
104 | Pazanan 2 | P-162 | Diff. Head (m) | 21.4 | 21.4 | PUMPS!B18 | Match
104 | Pazanan 2 | P-162 | Discharge Pressure (barg) | 2 | 2 | PUMPS!B18 | Match
104 | Pazanan 2 | P-162 | NACE | N | (no NACE line) |  | Inferred – marked
104 | Pazanan 2 | P-162 | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS!B18 | Match
104 | Pazanan 2 | P-162 | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
104 | Pazanan 2 | P-162 | Currency | EUR | EUR | PUMPS!F18 | Match
104 | Pazanan 2 | P-162 | Unit Price | 34500 | 34500 | PUMPS!F18 | Match
105 | Pazanan 2 | P-163 A/B | Equipment Name | O.W.S. Oil Pumps | O.W.S. Oil Pumps | PUMPS!B19 | Match
105 | Pazanan 2 | P-163 A/B | Quantity | 2 | 2 | PUMPS!C19 | Match
105 | Pazanan 2 | P-163 A/B | Pump Family | PD-Rotary (Progressing Cavity) | P.D.-Rotary (Progressing Cavity) | PUMPS!B19 | Match
105 | Pazanan 2 | P-163 A/B | Material Class | D-1 | D1 | PUMPS!B19 | Match
105 | Pazanan 2 | P-163 A/B | Capacity (m³/h) | 5 | 5 | PUMPS!B19 | Match
105 | Pazanan 2 | P-163 A/B | Discharge Pressure (barg) | 6.4 | 6.4 | PUMPS!B19 | Match
105 | Pazanan 2 | P-163 A/B | NACE | Y | Y | PUMPS!B19 | Match
105 | Pazanan 2 | P-163 A/B | Standard / IPS | API 676 + IPS-M-PM-140 | API 676 & IPS-M-PM-140 | PUMPS!B19 | Match
105 | Pazanan 2 | P-163 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
105 | Pazanan 2 | P-163 A/B | Currency | EUR | EUR | PUMPS!AR19/AQ19 | Match
105 | Pazanan 2 | P-163 A/B | Unit Price | 25000 | 25000 | PUMPS!AR19/AQ19 | Match
106 | Pazanan 2 | P-164 A/B | Equipment Name | O.W.S. Water Pumps | O.W.S. Water Pumps | PUMPS!B20 | Match
106 | Pazanan 2 | P-164 A/B | Quantity | 2 | 2 | PUMPS!C20 | Match
106 | Pazanan 2 | P-164 A/B | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS!B20 | Match
106 | Pazanan 2 | P-164 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS!B20 | Match
106 | Pazanan 2 | P-164 A/B | Material Class | D-2 | D2 | PUMPS!B20 | Match
106 | Pazanan 2 | P-164 A/B | Capacity (m³/h) | 15 | 15 | PUMPS!B20 | Match
106 | Pazanan 2 | P-164 A/B | Diff. Head (m) | 50 | 50 | PUMPS!B20 | Match
106 | Pazanan 2 | P-164 A/B | Discharge Pressure (barg) | 5.7 | 5.7 | PUMPS!B20 | Match
106 | Pazanan 2 | P-164 A/B | NACE | Y | Y | PUMPS!B20 | Match
106 | Pazanan 2 | P-164 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS!B20 | Match
106 | Pazanan 2 | P-164 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
106 | Pazanan 2 | P-164 A/B | Currency | EUR | EUR | PUMPS!F20 | Match
106 | Pazanan 2 | P-164 A/B | Unit Price | 29600 | 29600 | PUMPS!F20 | Match
107 | Pazanan 2 | P-165 A/B | Equipment Name | Oily Water Basin Pumps | Oily Water Basin Pumps | PUMPS!B21 | Match
107 | Pazanan 2 | P-165 A/B | Quantity | 2 | 2 | PUMPS!C21 | Match
107 | Pazanan 2 | P-165 A/B | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS!B21 | Match
107 | Pazanan 2 | P-165 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS!B21 | Match
107 | Pazanan 2 | P-165 A/B | Material Class | S-6 | S6 | PUMPS!B21 | Match
107 | Pazanan 2 | P-165 A/B | Capacity (m³/h) | 15 | 15 | PUMPS!B21 | Match
107 | Pazanan 2 | P-165 A/B | Diff. Head (m) | 20 | 20 | PUMPS!B21 | Match
107 | Pazanan 2 | P-165 A/B | Discharge Pressure (barg) | 2.5 | 2.5 | PUMPS!B21 | Match
107 | Pazanan 2 | P-165 A/B | NACE | N | (no NACE line) |  | Inferred – marked
107 | Pazanan 2 | P-165 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS!B21 | Match
107 | Pazanan 2 | P-165 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
107 | Pazanan 2 | P-165 A/B | Currency | EUR | EUR | PUMPS!F21 | Match
107 | Pazanan 2 | P-165 A/B | Unit Price | 26250 | 26250 | PUMPS!F21 | Match
108 | Pazanan 2 | P-171 | Equipment Name | Fuel Oil Pump | Fuel Oil Pump | PUMPS!B22 | Match
108 | Pazanan 2 | P-171 | Quantity | 1 | 1 | PUMPS!C22 | Match
108 | Pazanan 2 | P-171 | Pump Family | Centrifugal | Centrifugal (Horizontal) | PUMPS!B22 | Match
108 | Pazanan 2 | P-171 | Material Class | S-1 | S1 | PUMPS!B22 | Match
108 | Pazanan 2 | P-171 | Capacity (m³/h) | 10 | 10 | PUMPS!B22 | Match
108 | Pazanan 2 | P-171 | Diff. Head (m) | 21 | 21 | PUMPS!B22 | Match
108 | Pazanan 2 | P-171 | Discharge Pressure (barg) | 2 | 2 | PUMPS!B22 | Match
108 | Pazanan 2 | P-171 | NACE | N | (no NACE line) |  | Inferred – marked
108 | Pazanan 2 | P-171 | Standard / IPS | ISO 5199 + IPS-M-PM-115 | ISO 5199 & IPS-M-PM-115 | PUMPS!B22 | Match
108 | Pazanan 2 | P-171 | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
108 | Pazanan 2 | P-171 | Currency | EUR | EUR | PUMPS!F22 | Match
108 | Pazanan 2 | P-171 | Unit Price | 21000 | 21000 | PUMPS!F22 | Match
109 | Pazanan 2 | P-191 | Equipment Name | Fire Water Loading Pump | Fire Water Loading Pump | PUMPS!B23 | Match
109 | Pazanan 2 | P-191 | Quantity | 1 | 1 | PUMPS!C23 | Match
109 | Pazanan 2 | P-191 | Pump Family | Centrifugal | Centrifugal (Horizontal) | PUMPS!B23 | Match
109 | Pazanan 2 | P-191 | Material Class | I-2 | I2 | PUMPS!B23 | Match
109 | Pazanan 2 | P-191 | Capacity (m³/h) | 33 | 33 | PUMPS!B23 | Match
109 | Pazanan 2 | P-191 | Diff. Head (m) | 31 | 31 | PUMPS!B23 | Match
109 | Pazanan 2 | P-191 | Discharge Pressure (barg) | 2.9 | 2.9 | PUMPS!B23 | Match
109 | Pazanan 2 | P-191 | NACE | N | (no NACE line) |  | Inferred – marked
109 | Pazanan 2 | P-191 | Standard / IPS | ISO 5199 + IPS-M-PM-115 | ISO 5199 & IPS-M-PM-115 | PUMPS!B23 | Match
109 | Pazanan 2 | P-191 | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
109 | Pazanan 2 | P-191 | Currency | EUR | EUR | PUMPS!F23 | Match
109 | Pazanan 2 | P-191 | Unit Price | 16000 | 16000 | PUMPS!F23 | Match
110 | Pazanan 2 | P-192 | Equipment Name | Fire Water Pump-Elect. Motor Driven | Fire Water Pump-Elect. Motor Driven | PUMPS!B24 | Match
110 | Pazanan 2 | P-192 | Quantity | 1 | 1 | PUMPS!C24 | Match
110 | Pazanan 2 | P-192 | API 610 Type | BB (unspecified) | Centrifugal (Horizontal, Impeller Between Bearings Design) | PUMPS!B24 | Match
110 | Pazanan 2 | P-192 | Pump Family | Centrifugal | Centrifugal (Horizontal, Impeller Between Bearings Design) | PUMPS!B24 | Match
110 | Pazanan 2 | P-192 | Material Class | I-2 | I2 | PUMPS!B24 | Match
110 | Pazanan 2 | P-192 | Capacity (m³/h) | 825 | 825 | PUMPS!B24 | Match
110 | Pazanan 2 | P-192 | Diff. Head (m) | 107 | 107 | PUMPS!B24 | Match
110 | Pazanan 2 | P-192 | Discharge Pressure (barg) | 11.3 | 11.3 | PUMPS!B24 | Match
110 | Pazanan 2 | P-192 | NACE | N | (no NACE line) |  | Inferred – marked
110 | Pazanan 2 | P-192 | Standard / IPS | NFPA 20 + IPS-M-PM-125 | NFPA 20 & IPS-M-PM-125 | PUMPS!B24 | Match
110 | Pazanan 2 | P-192 | Driver Type | Electric Motor | name: electric | Equipment Name | Match
110 | Pazanan 2 | P-192 | Currency | EUR | EUR | PUMPS!F24 | Match
110 | Pazanan 2 | P-192 | Unit Price | 309660.11 | 309660.11 | PUMPS!F24 | Match
111 | Pazanan 2 | P-193 | Equipment Name | Fire Water Pump-Diesel Engine Driven | Fire Water Pump-Diesel Engine Driven | PUMPS!B25 | Match
111 | Pazanan 2 | P-193 | Quantity | 1 | 1 | PUMPS!C25 | Match
111 | Pazanan 2 | P-193 | API 610 Type | BB (unspecified) | Centrifugal (Horizontal, Impeller Between Bearings Design) | PUMPS!B25 | Match
111 | Pazanan 2 | P-193 | Pump Family | Centrifugal | Centrifugal (Horizontal, Impeller Between Bearings Design) | PUMPS!B25 | Match
111 | Pazanan 2 | P-193 | Material Class | I-2 | I2 | PUMPS!B25 | Match
111 | Pazanan 2 | P-193 | Capacity (m³/h) | 825 | 825 | PUMPS!B25 | Match
111 | Pazanan 2 | P-193 | Diff. Head (m) | 107 | 107 | PUMPS!B25 | Match
111 | Pazanan 2 | P-193 | Discharge Pressure (barg) | 11.3 | 11.3 | PUMPS!B25 | Match
111 | Pazanan 2 | P-193 | NACE | N | (no NACE line) |  | Inferred – marked
111 | Pazanan 2 | P-193 | Standard / IPS | NFPA 20 + IPS-M-PM-125 | NFPA 20 & IPS-M-PM-125 | PUMPS!B25 | Match
111 | Pazanan 2 | P-193 | Driver Type | Diesel Engine | name: diesel | Equipment Name | Match
111 | Pazanan 2 | P-193 | Currency | EUR | EUR | PUMPS!F25 | Match
111 | Pazanan 2 | P-193 | Unit Price | 202973.76 | 202973.7567 | PUMPS!F25 | Match
112 | Pazanan 2 | P-194 A/B | Equipment Name | Fire Water Jockey Pumps | Fire Water Jockey Pumps | PUMPS!B26 | Match
112 | Pazanan 2 | P-194 A/B | Quantity | 2 | 2 | PUMPS!C26 | Match
112 | Pazanan 2 | P-194 A/B | API 610 Type | OH (unspecified) | Centrifugal (Horizontal, Overhung Impeller Design) | PUMPS!B26 | Match
112 | Pazanan 2 | P-194 A/B | Pump Family | Centrifugal | Centrifugal (Horizontal, Overhung Impeller Design) | PUMPS!B26 | Match
112 | Pazanan 2 | P-194 A/B | Material Class | I-2 | I2 | PUMPS!B26 | Match
112 | Pazanan 2 | P-194 A/B | Capacity (m³/h) | 16.5 | 16.5 | PUMPS!B26 | Match
112 | Pazanan 2 | P-194 A/B | Diff. Head (m) | 107 | 107 | PUMPS!B26 | Match
112 | Pazanan 2 | P-194 A/B | Discharge Pressure (barg) | 11.3 | 11.3 | PUMPS!B26 | Match
112 | Pazanan 2 | P-194 A/B | NACE | N | (no NACE line) |  | Inferred – marked
112 | Pazanan 2 | P-194 A/B | Standard / IPS | NFPA 20 + IPS-M-PM-125 | NFPA 20 & IPS-M-PM-125 | PUMPS!B26 | Match
112 | Pazanan 2 | P-194 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
112 | Pazanan 2 | P-194 A/B | Currency | EUR | EUR | PUMPS!F26 | Match
112 | Pazanan 2 | P-194 A/B | Unit Price | 26808.07 | 26808.0667 | PUMPS!F26 | Match
113 | Pazanan 2 | P-210 A/B | Equipment Name | Chemical Loading Pumps | Chemical Loading Pumps | PUMPS!B27 | Match
113 | Pazanan 2 | P-210 A/B | Quantity | 2 | 2 | PUMPS!C27 | Match
113 | Pazanan 2 | P-210 A/B | Pump Family | Portable Barrel | Portable Barrel Pump | PUMPS!B27 | Match
113 | Pazanan 2 | P-210 A/B | Material Class | SS316L (non-API) | S.S. 316 L | PUMPS!B27 | Match
113 | Pazanan 2 | P-210 A/B | Capacity (m³/h) | 9.6 | 9.6 | PUMPS!B27 (L/min→m³/h) | Match
113 | Pazanan 2 | P-210 A/B | NACE | N | (no NACE line) |  | Inferred – marked
113 | Pazanan 2 | P-210 A/B | Driver Type | Portable (Air / Electric) | (not stated) |  | Inferred – marked
113 | Pazanan 2 | P-210 A/B | Currency | IRR | IRR | PUMPS!AR27/AQ27 | Match
113 | Pazanan 2 | P-210 A/B | Unit Price | 100000000 | 100000000 | PUMPS!AR27/AQ27 | Match
114 | Pazanan 2 | P-211 | Equipment Name | Chemical Loading Pumps | Chemical Loading Pumps | PUMPS!B28 | Match
114 | Pazanan 2 | P-211 | Quantity | 1 | 1 | PUMPS!C28 | Match
114 | Pazanan 2 | P-211 | Pump Family | Portable Barrel | Portable Barrel Pump | PUMPS!B28 | Match
114 | Pazanan 2 | P-211 | Material Class | SS316L (non-API) | S.S. 316 L | PUMPS!B28 | Match
114 | Pazanan 2 | P-211 | Capacity (m³/h) | 9.6 | 9.6 | PUMPS!B28 (L/min→m³/h) | Match
114 | Pazanan 2 | P-211 | NACE | N | (no NACE line) |  | Inferred – marked
114 | Pazanan 2 | P-211 | Driver Type | Portable (Air / Electric) | (not stated) |  | Inferred – marked
114 | Pazanan 2 | P-211 | Currency | IRR | IRR | PUMPS!AR28/AQ28 | Match
114 | Pazanan 2 | P-211 | Unit Price | 100000000 | 100000000 | PUMPS!AR28/AQ28 | Match
115 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Equipment Name | 2nd Stage Separators Oil Pumps | 2nd Stage Separators Oil Pumps | PUMPS!B4 | Match
115 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Pump Family | Centrifugal | Centrifugal | PUMPS!D4 | Match
115 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Diff. Head (m) | 95.8 | 95.8 | PUMPS!F4 | Match
115 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Power (kW) | 54.3 | 54.3 | PUMPS!G4 | Match
115 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Driver Type | Electric Motor | Electric Motor | PUMPS!E4 | Match
115 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Currency | USD | USD | PUMPS!H4 | Match
115 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Unit Price | 580000 | 580000 | PUMPS!H4 | Match
116 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Equipment Name | 3rd Stage Separators Oil Pumps | 3rd Stage Separators Oil Pumps | PUMPS!B5 | Match
116 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Pump Family | Centrifugal | Centrifugal | PUMPS!D5 | Match
116 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Diff. Head (m) | 59.85 | 59.85 | PUMPS!F5 | Match
116 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Power (kW) | 33.12 | 33.12 | PUMPS!G5 | Match
116 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Driver Type | Electric Motor | Electric Motor | PUMPS!E5 | Match
116 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Currency | USD | USD | PUMPS!H5 | Match
116 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Unit Price | 380000 | 380000 | PUMPS!H5 | Match
117 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Equipment Name | Stabilized Oil Pump | Stabilized Oil Pump | PUMPS!B6 | Match
117 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Pump Family | Centrifugal | Centrifugal | PUMPS!D6 | Match
117 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Diff. Head (m) | 34.75 | 34.75 | PUMPS!F6 | Match
117 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Power (kW) | 57.35 | 57.35 | PUMPS!G6 | Match
117 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Driver Type | Electric Motor | Electric Motor | PUMPS!E6 | Match
117 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Currency | USD | USD | PUMPS!H6 | Match
117 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Unit Price | 250000 | 250000 | PUMPS!H6 | Match
118 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Equipment Name | Product Oil Pump | Product Oil Pump | PUMPS!B7 | Match
118 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Pump Family | Centrifugal | Centrifugal | PUMPS!D7 | Match
118 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Driver Type | Electric Motor | Electric Motor | PUMPS!E7 | Match
118 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Currency | USD | USD | PUMPS!H7 | Match
118 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Unit Price | 320000 | 320000 | PUMPS!H7 | Match
119 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Equipment Name | Off Spec Crude Pump | Off Spec Crude Pump | PUMPS!B8 | Match
119 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Pump Family | Centrifugal | Centrifugal | PUMPS!D8 | Match
119 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Diff. Head (m) | 311.3 | 311.3 | PUMPS!F8 | Match
119 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Power (kW) | 48 | 48 | PUMPS!G8 | Match
119 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Driver Type | Electric Motor | Electric Motor | PUMPS!E8 | Match
119 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Currency | USD | USD | PUMPS!H8 | Match
119 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Unit Price | 75000 | 75000 | PUMPS!H8 | Match
120 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Equipment Name | Second Stage Desalter Water Criculated Pump | Second Stage Desalter Water Criculated Pump | PUMPS!B9 | Match
120 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Pump Family | Centrifugal | Centrifugal | PUMPS!D9 | Match
120 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Diff. Head (m) | 32 | 32 | PUMPS!F9 | Match
120 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Power (kW) | 1 | 1 | PUMPS!G9 | Match
120 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Driver Type | Electric Motor | Electric Motor | PUMPS!E9 | Match
120 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Currency | USD | USD | PUMPS!H9 | Match
120 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Unit Price | 60000 | 60000 | PUMPS!H9 | Match
121 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Equipment Name | Degassing Water Pump | Degassing Water Pump | PUMPS!B10 | Match
121 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Pump Family | Centrifugal | Centrifugal | PUMPS!D10 | Match
121 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Diff. Head (m) | 36.15 | 36.15 | PUMPS!F10 | Match
121 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Power (kW) | 13.1 | 13.1 | PUMPS!G10 | Match
121 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Driver Type | Electric Motor | Electric Motor | PUMPS!E10 | Match
121 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Currency | USD | USD | PUMPS!H10 | Match
121 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Unit Price | 60000 | 60000 | PUMPS!H10 | Match
122 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Equipment Name | Disposal Water Pump | Disposal Water Pump | PUMPS!B11 | Match
122 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Pump Family | Centrifugal | Centrifugal | PUMPS!D11 | Match
122 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Diff. Head (m) | 51.5 | 51.5 | PUMPS!F11 | Match
122 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Driver Type | Electric Motor | Electric Motor | PUMPS!E11 | Match
122 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Currency | USD | USD | PUMPS!H11 | Match
122 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Unit Price | 10000 | 10000 | PUMPS!H11 | Match
123 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Equipment Name | Fresh Water Pump | Fresh Water Pump | PUMPS!B12 | Match
123 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Pump Family | Centrifugal | Centrifugal | PUMPS!D12 | Match
123 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Diff. Head (m) | 41 | 41 | PUMPS!F12 | Match
123 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Power (kW) | 3.9 | 3.9 | PUMPS!G12 | Match
123 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Driver Type | Electric Motor | Electric Motor | PUMPS!E12 | Match
123 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Currency | USD | USD | PUMPS!H12 | Match
123 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Unit Price | 8000 | 8000 | PUMPS!H12 | Match
124 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Equipment Name | Closed Drain Pump | Closed Drain Pump | PUMPS!B13 | Match
124 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Diff. Head (m) | 120 | 120 | PUMPS!F13 | Match
124 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Power (kW) | 13.7 | 13.7 | PUMPS!G13 | Match
124 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Driver Type | Electric Motor | Electric Motor | PUMPS!E13 | Match
124 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Currency | USD | USD | PUMPS!H13 | Match
124 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Unit Price | 40000 | 40000 | PUMPS!H13 | Match
125 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Equipment Name | Diesel Unlodaing pump | Diesel Unlodaing pump | PUMPS!B14 | Match
125 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Pump Family | PD-Rotary (Sliding Vane) | Sliding valve | PUMPS!D14 | Match
125 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Diff. Head (m) | 27.2 | 27.2 | PUMPS!F14 | Match
125 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Driver Type | Not stated | Not stated | PUMPS!E14 | Match
125 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Currency | USD | USD | PUMPS!H14 | Match
125 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Unit Price | 5000 | 5000 | PUMPS!H14 | Match
126 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Equipment Name | Diesel Transfer pump | Diesel Transfer pump | PUMPS!B15 | Match
126 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Pump Family | PD-Rotary (Screw) | Screw | PUMPS!D15 | Match
126 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Diff. Head (m) | 40.8 | 40.8 | PUMPS!F15 | Match
126 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Power (kW) | 0.83 | 0.83 | PUMPS!G15 | Match
126 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Driver Type | Electric Motor | Electric Motor | PUMPS!E15 | Match
126 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Currency | USD | USD | PUMPS!H15 | Match
126 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Unit Price | 3000 | 3000 | PUMPS!H15 | Match
127 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Equipment Name | Sludge Discharge Water Jet Pump | Sludge Discharge Water Jet Pump | PUMPS!B16 | Match
127 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Pump Family | Centrifugal | Centrifugal | PUMPS!D16 | Match
127 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Driver Type | Electric Motor | Electric Motor | PUMPS!E16 | Match
127 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Currency | USD | USD | PUMPS!H16 | Match
127 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Unit Price | 3000 | 3000 | PUMPS!H16 | Match
128 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Equipment Name | Flare KO Drum Pumps | Flare KO Drum Pumps | PUMPS!B17 | Match
128 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Pump Family | Centrifugal | Centrifugal | PUMPS!D17 | Match
128 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Driver Type | Electric Motor | Electric Motor | PUMPS!E17 | Match
128 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Currency | USD | USD | PUMPS!H17 | Match
128 | (نام پروژه در فایل قید نشده است) – نمونه قیمتی نمک زدایی (PUMPS.csv) | (Not stated in source document) | Unit Price | 40000 | 40000 | PUMPS!H17 | Match
129 | Pazanan 2 | P-111 A/B | Equipment Name | Off Spec. Crude Pumps | Off Spec. Crude Pumps | PUMPS!B8 | Match
129 | Pazanan 2 | P-111 A/B | Quantity | 2 | 2 | PUMPS!C8 | Match
129 | Pazanan 2 | P-111 A/B | API 610 Type | VS6 | Centrifugal (VS6) | PUMPS!B8 | Match
129 | Pazanan 2 | P-111 A/B | Pump Family | Centrifugal | Centrifugal (VS6) | PUMPS!B8 | Match
129 | Pazanan 2 | P-111 A/B | Material Class | D-1 | D1 | PUMPS!B8 | Match
129 | Pazanan 2 | P-111 A/B | Capacity (m³/h) | 45 | 45 | PUMPS!B8 | Match
129 | Pazanan 2 | P-111 A/B | Diff. Head (m) | 139.1 | 139.1 | PUMPS!B8 | Match
129 | Pazanan 2 | P-111 A/B | Discharge Pressure (barg) | 14.5 | 14.5 | PUMPS!B8 | Match
129 | Pazanan 2 | P-111 A/B | NACE | Y | Y | PUMPS!B8 | Match
129 | Pazanan 2 | P-111 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS!B8 | Match
129 | Pazanan 2 | P-111 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
129 | Pazanan 2 | P-111 A/B | Currency | EUR | EUR | PUMPS!AR8/AQ8 | Match
129 | Pazanan 2 | P-111 A/B | Unit Price | 75000 | 75000 | PUMPS!AR8/AQ8 | Match
130 | Pazanan 2 | P-122 A/B | Equipment Name | Deaerated Water Pumps | Deaerated Water Pumps | PUMPS!B9 | Match
130 | Pazanan 2 | P-122 A/B | Quantity | 2 | 2 | PUMPS!C9 | Match
130 | Pazanan 2 | P-122 A/B | Pump Family | Centrifugal | Centrifugal (Horizontal) | PUMPS!B9 | Match
130 | Pazanan 2 | P-122 A/B | Material Class | I-2 | I2 | PUMPS!B9 | Match
130 | Pazanan 2 | P-122 A/B | Capacity (m³/h) | 53 | 53 | PUMPS!B9 | Match
130 | Pazanan 2 | P-122 A/B | Diff. Head (m) | 35.7 | 35.7 | PUMPS!B9 | Match
130 | Pazanan 2 | P-122 A/B | Discharge Pressure (barg) | 2.9 | 2.9 | PUMPS!B9 | Match
130 | Pazanan 2 | P-122 A/B | NACE | N | (no NACE line) |  | Inferred – marked
130 | Pazanan 2 | P-122 A/B | Standard / IPS | ISO 5199 + IPS-M-PM-115 | ISO 5199 & IPS-M-PM-115 | PUMPS!B9 | Match
130 | Pazanan 2 | P-122 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
130 | Pazanan 2 | P-122 A/B | Currency | EUR | EUR | PUMPS!AR9/AQ9 | Match
130 | Pazanan 2 | P-122 A/B | Unit Price | 10000 | 10000 | PUMPS!AR9/AQ9 | Match
131 | Pazanan 2 | P-124 | Equipment Name | Dilution Water Pump | Dilution Water Pump | PUMPS!B10 | Match
131 | Pazanan 2 | P-124 | Quantity | 1 | 1 | PUMPS!C10 | Match
131 | Pazanan 2 | P-124 | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS!B10 | Match
131 | Pazanan 2 | P-124 | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS!B10 | Match
131 | Pazanan 2 | P-124 | Material Class | I-2 | I2 | PUMPS!B10 | Match
131 | Pazanan 2 | P-124 | Capacity (m³/h) | 53 | 53 | PUMPS!B10 | Match
131 | Pazanan 2 | P-124 | Diff. Head (m) | 122.3 | 122.3 | PUMPS!B10 | Match
131 | Pazanan 2 | P-124 | Discharge Pressure (barg) | 12 | 12 | PUMPS!B10 | Match
131 | Pazanan 2 | P-124 | NACE | N | (no NACE line) |  | Inferred – marked
131 | Pazanan 2 | P-124 | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS!B10 | Match
131 | Pazanan 2 | P-124 | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
131 | Pazanan 2 | P-124 | Currency | EUR | EUR | PUMPS!AR10/AQ10 | Match
131 | Pazanan 2 | P-124 | Unit Price | 15000 | 15000 | PUMPS!AR10/AQ10 | Match
132 | Pazanan 2 | P-125 A/B | Equipment Name | Dilution Water Pumps | Dilution Water Pumps | PUMPS!B11 | Match
132 | Pazanan 2 | P-125 A/B | Quantity | 2 | 2 | PUMPS!C11 | Match
132 | Pazanan 2 | P-125 A/B | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS!B11 | Match
132 | Pazanan 2 | P-125 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS!B11 | Match
132 | Pazanan 2 | P-125 A/B | Material Class | I-2 | I2 | PUMPS!B11 | Match
132 | Pazanan 2 | P-125 A/B | Capacity (m³/h) | 31 | 31 | PUMPS!B11 | Match
132 | Pazanan 2 | P-125 A/B | Diff. Head (m) | 122 | 122 | PUMPS!B11 | Match
132 | Pazanan 2 | P-125 A/B | Discharge Pressure (barg) | 13 | 13 | PUMPS!B11 | Match
132 | Pazanan 2 | P-125 A/B | NACE | N | (no NACE line) |  | Inferred – marked
132 | Pazanan 2 | P-125 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS!B11 | Match
132 | Pazanan 2 | P-125 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
132 | Pazanan 2 | P-125 A/B | Currency | EUR | EUR | PUMPS!AR11/AQ11 | Match
132 | Pazanan 2 | P-125 A/B | Unit Price | 12000 | 12000 | PUMPS!AR11/AQ11 | Match
133 | Pazanan 2 | P-136 A/B | Equipment Name | Disposal Water InjectionPumps | Disposal Water InjectionPumps | PUMPS!B12 | Match
133 | Pazanan 2 | P-136 A/B | Quantity | 2 | 2 | PUMPS!C12 | Match
133 | Pazanan 2 | P-136 A/B | API 610 Type | BB3 | Centrifugal (BB3) | PUMPS!B12 | Match
133 | Pazanan 2 | P-136 A/B | Pump Family | Centrifugal | Centrifugal (BB3) | PUMPS!B12 | Match
133 | Pazanan 2 | P-136 A/B | Material Class | D-2 | D2 | PUMPS!B12 | Match
133 | Pazanan 2 | P-136 A/B | Capacity (m³/h) | 91 | 91 | PUMPS!B12 | Match
133 | Pazanan 2 | P-136 A/B | Diff. Head (m) | 650 | 650 | PUMPS!B12 | Match
133 | Pazanan 2 | P-136 A/B | Discharge Pressure (barg) | 72.8 | 72.8 | PUMPS!B12 | Match
133 | Pazanan 2 | P-136 A/B | NACE | Y | Y | PUMPS!B12 | Match
133 | Pazanan 2 | P-136 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS!B12 | Match
133 | Pazanan 2 | P-136 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
133 | Pazanan 2 | P-136 A/B | Currency | EUR | EUR | PUMPS!AR12/AQ12 | Match
133 | Pazanan 2 | P-136 A/B | Unit Price | 260000 | 260000 | PUMPS!AR12/AQ12 | Match
134 | Pazanan 2 | P-137 A/B | Equipment Name | Dirty Oil Pumps | Dirty Oil Pumps | PUMPS!B13 | Match
134 | Pazanan 2 | P-137 A/B | Quantity | 2 | 2 | PUMPS!C13 | Match
134 | Pazanan 2 | P-137 A/B | Pump Family | PD-Rotary (Gear) | P.D.-Rotary (Ext. Gear) | PUMPS!B13 | Match
134 | Pazanan 2 | P-137 A/B | Material Class | D-1 | D1 | PUMPS!B13 | Match
134 | Pazanan 2 | P-137 A/B | Capacity (m³/h) | 5 | 5 | PUMPS!B13 | Match
134 | Pazanan 2 | P-137 A/B | Discharge Pressure (barg) | 8 | 8 | PUMPS!B13 | Match
134 | Pazanan 2 | P-137 A/B | NACE | Y | Y | PUMPS!B13 | Match
134 | Pazanan 2 | P-137 A/B | Standard / IPS | API 676 + IPS-M-PM-140 | API 676 & IPS-M-PM-140 | PUMPS!B13 | Match
134 | Pazanan 2 | P-137 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
134 | Pazanan 2 | P-137 A/B | Currency | EUR | EUR | PUMPS!AR13/AQ13 | Match
134 | Pazanan 2 | P-137 A/B | Unit Price | 10000 | 10000 | PUMPS!AR13/AQ13 | Match
135 | Pazanan 2 | P-138 A/B | Equipment Name | Evaporation Pond Water Return Pumps | Evaporation Pond Water Return Pumps | PUMPS!B14 | Match
135 | Pazanan 2 | P-138 A/B | Quantity | 2 | 2 | PUMPS!C14 | Match
135 | Pazanan 2 | P-138 A/B | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS!B14 | Match
135 | Pazanan 2 | P-138 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS!B14 | Match
135 | Pazanan 2 | P-138 A/B | Material Class | D-2 | D2 | PUMPS!B14 | Match
135 | Pazanan 2 | P-138 A/B | Capacity (m³/h) | 15 | 15 | PUMPS!B14 | Match
135 | Pazanan 2 | P-138 A/B | Diff. Head (m) | 27 | 27 | PUMPS!B14 | Match
135 | Pazanan 2 | P-138 A/B | Discharge Pressure (barg) | 3.2 | 3.2 | PUMPS!B14 | Match
135 | Pazanan 2 | P-138 A/B | NACE | N | (no NACE line) |  | Inferred – marked
135 | Pazanan 2 | P-138 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS!B14 | Match
135 | Pazanan 2 | P-138 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
135 | Pazanan 2 | P-138 A/B | Currency | EUR | EUR | PUMPS!AR14/AQ14 | Match
135 | Pazanan 2 | P-138 A/B | Unit Price | 35000 | 35000 | PUMPS!AR14/AQ14 | Match
136 | Pazanan 2 | P-139 A/B/C | Equipment Name | Disposal Water InjectionPumps | Disposal Water InjectionPumps | PUMPS!B15 | Match
136 | Pazanan 2 | P-139 A/B/C | Quantity | 3 | 3 | PUMPS!C15 | Match
136 | Pazanan 2 | P-139 A/B/C | API 610 Type | BB3 | Centrifugal (BB3) | PUMPS!B15 | Match
136 | Pazanan 2 | P-139 A/B/C | Pump Family | Centrifugal | Centrifugal (BB3) | PUMPS!B15 | Match
136 | Pazanan 2 | P-139 A/B/C | Material Class | D-2 | D2 | PUMPS!B15 | Match
136 | Pazanan 2 | P-139 A/B/C | Capacity (m³/h) | 44 | 44 | PUMPS!B15 | Match
136 | Pazanan 2 | P-139 A/B/C | Diff. Head (m) | 385 | 385 | PUMPS!B15 | Match
136 | Pazanan 2 | P-139 A/B/C | Discharge Pressure (barg) | 48.2 | 48.2 | PUMPS!B15 | Match
136 | Pazanan 2 | P-139 A/B/C | NACE | Y | Y | PUMPS!B15 | Match
136 | Pazanan 2 | P-139 A/B/C | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS!B15 | Match
136 | Pazanan 2 | P-139 A/B/C | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
136 | Pazanan 2 | P-139 A/B/C | Currency | EUR | EUR | PUMPS!AR15/AQ15 | Match
136 | Pazanan 2 | P-139 A/B/C | Unit Price | 180000 | 180000 | PUMPS!AR15/AQ15 | Match
137 | Pazanan 2 | P-151 A/B | Equipment Name | Flare K.O. Drum Pumps | Flare K.O. Drum Pumps | PUMPS!B16 | Match
137 | Pazanan 2 | P-151 A/B | Quantity | 2 | 2 | PUMPS!C16 | Match
137 | Pazanan 2 | P-151 A/B | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS!B16 | Match
137 | Pazanan 2 | P-151 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS!B16 | Match
137 | Pazanan 2 | P-151 A/B | Material Class | S-6 | S6 | PUMPS!B16 | Match
137 | Pazanan 2 | P-151 A/B | Capacity (m³/h) | 10 | 10 | PUMPS!B16 | Match
137 | Pazanan 2 | P-151 A/B | Diff. Head (m) | 40 | 40 | PUMPS!B16 | Match
137 | Pazanan 2 | P-151 A/B | Discharge Pressure (barg) | 6.8 | 6.8 | PUMPS!B16 | Match
137 | Pazanan 2 | P-151 A/B | NACE | N | (no NACE line) |  | Inferred – marked
137 | Pazanan 2 | P-151 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS!B16 | Match
137 | Pazanan 2 | P-151 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
137 | Pazanan 2 | P-151 A/B | Currency | EUR | EUR | PUMPS!AR16/AQ16 | Match
137 | Pazanan 2 | P-151 A/B | Unit Price | 15000 | 15000 | PUMPS!AR16/AQ16 | Match
138 | Pazanan 2 | P-161 A/B | Equipment Name | Closed Drain Drum Pumps | Closed Drain Drum Pumps | PUMPS!B17 | Match
138 | Pazanan 2 | P-161 A/B | Quantity | 2 | 2 | PUMPS!C17 | Match
138 | Pazanan 2 | P-161 A/B | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS!B17 | Match
138 | Pazanan 2 | P-161 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS!B17 | Match
138 | Pazanan 2 | P-161 A/B | Material Class | D-2 | D2 | PUMPS!B17 | Match
138 | Pazanan 2 | P-161 A/B | Capacity (m³/h) | 25 | 25 | PUMPS!B17 | Match
138 | Pazanan 2 | P-161 A/B | Diff. Head (m) | 55 | 55 | PUMPS!B17 | Match
138 | Pazanan 2 | P-161 A/B | Discharge Pressure (barg) | 5 | 5 | PUMPS!B17 | Match
138 | Pazanan 2 | P-161 A/B | NACE | Y | Y | PUMPS!B17 | Match
138 | Pazanan 2 | P-161 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS!B17 | Match
138 | Pazanan 2 | P-161 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
138 | Pazanan 2 | P-161 A/B | Currency | EUR | EUR | PUMPS!AR17/AQ17 | Match
138 | Pazanan 2 | P-161 A/B | Unit Price | 32000 | 32000 | PUMPS!AR17/AQ17 | Match
139 | Pazanan 2 | P-162 | Equipment Name | C. D. Drum / Flare K.O. Drum Sump Pump | C. D. Drum / Flare K.O. Drum Sump Pump | PUMPS!B18 | Match
139 | Pazanan 2 | P-162 | Quantity | 1 | 1 | PUMPS!C18 | Match
139 | Pazanan 2 | P-162 | API 610 Type | VS4 | Centrifugal (VS4) | PUMPS!B18 | Match
139 | Pazanan 2 | P-162 | Pump Family | Centrifugal | Centrifugal (VS4) | PUMPS!B18 | Match
139 | Pazanan 2 | P-162 | Material Class | S-6 | S6 | PUMPS!B18 | Match
139 | Pazanan 2 | P-162 | Capacity (m³/h) | 5 | 5 | PUMPS!B18 | Match
139 | Pazanan 2 | P-162 | Diff. Head (m) | 21.4 | 21.4 | PUMPS!B18 | Match
139 | Pazanan 2 | P-162 | Discharge Pressure (barg) | 2 | 2 | PUMPS!B18 | Match
139 | Pazanan 2 | P-162 | NACE | N | (no NACE line) |  | Inferred – marked
139 | Pazanan 2 | P-162 | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS!B18 | Match
139 | Pazanan 2 | P-162 | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
139 | Pazanan 2 | P-162 | Currency | EUR | EUR | PUMPS!AR18/AQ18 | Match
139 | Pazanan 2 | P-162 | Unit Price | 15000 | 15000 | PUMPS!AR18/AQ18 | Match
140 | Pazanan 2 | P-164 A/B | Equipment Name | O.W.S. Water Pumps | O.W.S. Water Pumps | PUMPS!B20 | Match
140 | Pazanan 2 | P-164 A/B | Quantity | 2 | 2 | PUMPS!C20 | Match
140 | Pazanan 2 | P-164 A/B | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS!B20 | Match
140 | Pazanan 2 | P-164 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS!B20 | Match
140 | Pazanan 2 | P-164 A/B | Material Class | D-2 | D2 | PUMPS!B20 | Match
140 | Pazanan 2 | P-164 A/B | Capacity (m³/h) | 15 | 15 | PUMPS!B20 | Match
140 | Pazanan 2 | P-164 A/B | Diff. Head (m) | 50 | 50 | PUMPS!B20 | Match
140 | Pazanan 2 | P-164 A/B | Discharge Pressure (barg) | 5.7 | 5.7 | PUMPS!B20 | Match
140 | Pazanan 2 | P-164 A/B | NACE | Y | Y | PUMPS!B20 | Match
140 | Pazanan 2 | P-164 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS!B20 | Match
140 | Pazanan 2 | P-164 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
140 | Pazanan 2 | P-164 A/B | Currency | EUR | EUR | PUMPS!AR20/AQ20 | Match
140 | Pazanan 2 | P-164 A/B | Unit Price | 15000 | 15000 | PUMPS!AR20/AQ20 | Match
141 | Pazanan 2 | P-165 A/B | Equipment Name | Oily Water Basin Pumps | Oily Water Basin Pumps | PUMPS!B21 | Match
141 | Pazanan 2 | P-165 A/B | Quantity | 2 | 2 | PUMPS!C21 | Match
141 | Pazanan 2 | P-165 A/B | API 610 Type | OH2 | Centrifugal (OH2) | PUMPS!B21 | Match
141 | Pazanan 2 | P-165 A/B | Pump Family | Centrifugal | Centrifugal (OH2) | PUMPS!B21 | Match
141 | Pazanan 2 | P-165 A/B | Material Class | S-6 | S6 | PUMPS!B21 | Match
141 | Pazanan 2 | P-165 A/B | Capacity (m³/h) | 15 | 15 | PUMPS!B21 | Match
141 | Pazanan 2 | P-165 A/B | Diff. Head (m) | 20 | 20 | PUMPS!B21 | Match
141 | Pazanan 2 | P-165 A/B | Discharge Pressure (barg) | 2.5 | 2.5 | PUMPS!B21 | Match
141 | Pazanan 2 | P-165 A/B | NACE | N | (no NACE line) |  | Inferred – marked
141 | Pazanan 2 | P-165 A/B | Standard / IPS | API 610 + IPS-G-PM-105 | API 610 & IPS-G-PM-105 | PUMPS!B21 | Match
141 | Pazanan 2 | P-165 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
141 | Pazanan 2 | P-165 A/B | Currency | EUR | EUR | PUMPS!AR21/AQ21 | Match
141 | Pazanan 2 | P-165 A/B | Unit Price | 15000 | 15000 | PUMPS!AR21/AQ21 | Match
142 | Pazanan 2 | P-171 | Equipment Name | Fuel Oil Pump | Fuel Oil Pump | PUMPS!B22 | Match
142 | Pazanan 2 | P-171 | Quantity | 1 | 1 | PUMPS!C22 | Match
142 | Pazanan 2 | P-171 | Pump Family | Centrifugal | Centrifugal (Horizontal) | PUMPS!B22 | Match
142 | Pazanan 2 | P-171 | Material Class | S-1 | S1 | PUMPS!B22 | Match
142 | Pazanan 2 | P-171 | Capacity (m³/h) | 10 | 10 | PUMPS!B22 | Match
142 | Pazanan 2 | P-171 | Diff. Head (m) | 21 | 21 | PUMPS!B22 | Match
142 | Pazanan 2 | P-171 | Discharge Pressure (barg) | 2 | 2 | PUMPS!B22 | Match
142 | Pazanan 2 | P-171 | NACE | N | (no NACE line) |  | Inferred – marked
142 | Pazanan 2 | P-171 | Standard / IPS | ISO 5199 + IPS-M-PM-115 | ISO 5199 & IPS-M-PM-115 | PUMPS!B22 | Match
142 | Pazanan 2 | P-171 | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
142 | Pazanan 2 | P-171 | Currency | EUR | EUR | PUMPS!AR22/AQ22 | Match
142 | Pazanan 2 | P-171 | Unit Price | 10000 | 10000 | PUMPS!AR22/AQ22 | Match
143 | Pazanan 2 | P-191 | Equipment Name | Fire Water Loading Pump | Fire Water Loading Pump | PUMPS!B23 | Match
143 | Pazanan 2 | P-191 | Quantity | 1 | 1 | PUMPS!C23 | Match
143 | Pazanan 2 | P-191 | Pump Family | Centrifugal | Centrifugal (Horizontal) | PUMPS!B23 | Match
143 | Pazanan 2 | P-191 | Material Class | I-2 | I2 | PUMPS!B23 | Match
143 | Pazanan 2 | P-191 | Capacity (m³/h) | 33 | 33 | PUMPS!B23 | Match
143 | Pazanan 2 | P-191 | Diff. Head (m) | 31 | 31 | PUMPS!B23 | Match
143 | Pazanan 2 | P-191 | Discharge Pressure (barg) | 2.9 | 2.9 | PUMPS!B23 | Match
143 | Pazanan 2 | P-191 | NACE | N | (no NACE line) |  | Inferred – marked
143 | Pazanan 2 | P-191 | Standard / IPS | ISO 5199 + IPS-M-PM-115 | ISO 5199 & IPS-M-PM-115 | PUMPS!B23 | Match
143 | Pazanan 2 | P-191 | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
143 | Pazanan 2 | P-191 | Currency | EUR | EUR | PUMPS!AR23/AQ23 | Match
143 | Pazanan 2 | P-191 | Unit Price | 6500 | 6500 | PUMPS!AR23/AQ23 | Match
144 | Pazanan 2 | P-192 | Equipment Name | Fire Water Pump-Elect. Motor Driven | Fire Water Pump-Elect. Motor Driven | PUMPS!B24 | Match
144 | Pazanan 2 | P-192 | Quantity | 1 | 1 | PUMPS!C24 | Match
144 | Pazanan 2 | P-192 | API 610 Type | BB (unspecified) | Centrifugal (Horizontal, Impeller Between Bearings Design) | PUMPS!B24 | Match
144 | Pazanan 2 | P-192 | Pump Family | Centrifugal | Centrifugal (Horizontal, Impeller Between Bearings Design) | PUMPS!B24 | Match
144 | Pazanan 2 | P-192 | Material Class | I-2 | I2 | PUMPS!B24 | Match
144 | Pazanan 2 | P-192 | Capacity (m³/h) | 825 | 825 | PUMPS!B24 | Match
144 | Pazanan 2 | P-192 | Diff. Head (m) | 107 | 107 | PUMPS!B24 | Match
144 | Pazanan 2 | P-192 | Discharge Pressure (barg) | 11.3 | 11.3 | PUMPS!B24 | Match
144 | Pazanan 2 | P-192 | NACE | N | (no NACE line) |  | Inferred – marked
144 | Pazanan 2 | P-192 | Standard / IPS | NFPA 20 + IPS-M-PM-125 | NFPA 20 & IPS-M-PM-125 | PUMPS!B24 | Match
144 | Pazanan 2 | P-192 | Driver Type | Electric Motor | name: electric | Equipment Name | Match
144 | Pazanan 2 | P-192 | Currency | EUR | EUR | PUMPS!AR24/AQ24 | Match
144 | Pazanan 2 | P-192 | Unit Price | 80000 | 80000 | PUMPS!AR24/AQ24 | Match
145 | Pazanan 2 | P-193 | Equipment Name | Fire Water Pump-Diesel Engine Driven | Fire Water Pump-Diesel Engine Driven | PUMPS!B25 | Match
145 | Pazanan 2 | P-193 | Quantity | 1 | 1 | PUMPS!C25 | Match
145 | Pazanan 2 | P-193 | API 610 Type | BB (unspecified) | Centrifugal (Horizontal, Impeller Between Bearings Design) | PUMPS!B25 | Match
145 | Pazanan 2 | P-193 | Pump Family | Centrifugal | Centrifugal (Horizontal, Impeller Between Bearings Design) | PUMPS!B25 | Match
145 | Pazanan 2 | P-193 | Material Class | I-2 | I2 | PUMPS!B25 | Match
145 | Pazanan 2 | P-193 | Capacity (m³/h) | 825 | 825 | PUMPS!B25 | Match
145 | Pazanan 2 | P-193 | Diff. Head (m) | 107 | 107 | PUMPS!B25 | Match
145 | Pazanan 2 | P-193 | Discharge Pressure (barg) | 11.3 | 11.3 | PUMPS!B25 | Match
145 | Pazanan 2 | P-193 | NACE | N | (no NACE line) |  | Inferred – marked
145 | Pazanan 2 | P-193 | Standard / IPS | NFPA 20 + IPS-M-PM-125 | NFPA 20 & IPS-M-PM-125 | PUMPS!B25 | Match
145 | Pazanan 2 | P-193 | Driver Type | Diesel Engine | name: diesel | Equipment Name | Match
145 | Pazanan 2 | P-193 | Currency | EUR | EUR | PUMPS!AR25/AQ25 | Match
145 | Pazanan 2 | P-193 | Unit Price | 100000 | 100000 | PUMPS!AR25/AQ25 | Match
146 | Pazanan 2 | P-194 A/B | Equipment Name | Fire Water Jockey Pumps | Fire Water Jockey Pumps | PUMPS!B26 | Match
146 | Pazanan 2 | P-194 A/B | Quantity | 2 | 2 | PUMPS!C26 | Match
146 | Pazanan 2 | P-194 A/B | API 610 Type | OH (unspecified) | Centrifugal (Horizontal, Overhung Impeller Design) | PUMPS!B26 | Match
146 | Pazanan 2 | P-194 A/B | Pump Family | Centrifugal | Centrifugal (Horizontal, Overhung Impeller Design) | PUMPS!B26 | Match
146 | Pazanan 2 | P-194 A/B | Material Class | I-2 | I2 | PUMPS!B26 | Match
146 | Pazanan 2 | P-194 A/B | Capacity (m³/h) | 16.5 | 16.5 | PUMPS!B26 | Match
146 | Pazanan 2 | P-194 A/B | Diff. Head (m) | 107 | 107 | PUMPS!B26 | Match
146 | Pazanan 2 | P-194 A/B | Discharge Pressure (barg) | 11.3 | 11.3 | PUMPS!B26 | Match
146 | Pazanan 2 | P-194 A/B | NACE | N | (no NACE line) |  | Inferred – marked
146 | Pazanan 2 | P-194 A/B | Standard / IPS | NFPA 20 + IPS-M-PM-125 | NFPA 20 & IPS-M-PM-125 | PUMPS!B26 | Match
146 | Pazanan 2 | P-194 A/B | Driver Type | Electric Motor | (not stated) |  | Inferred – marked
146 | Pazanan 2 | P-194 A/B | Currency | EUR | EUR | PUMPS!AR26/AQ26 | Match
146 | Pazanan 2 | P-194 A/B | Unit Price | 15000 | 15000 | PUMPS!AR26/AQ26 | Match

## Change_Log
CHANGE_LOG
Type | Field / Record | Change
Structure | Master Database | 28 → 72 columns in 7 groups (A–G); sub-category sheets replaced by AutoFilter on Master
Split | Weight / Power | Split into Power (kW) + Power Basis; "(Shaft)" → Shaft (Absorbed); HOLD → blank + remark
Split | Capacity / Pressure / Head | Text converted to numeric columns (m³/h, barg, m); original text kept in Remarks where relevant
Mapping | Type → Pump Family + API 610 Type | OH2/BB3/VS4/VS6 parsed; "Centrifugal (assumed)" → Family=Centrifugal, Type=Not stated
Mapping | Material Class | D1/D2/I2/S1/S5/S6 → API 610 Annex H codes D-1/D-2/I-2/S-1/S-5/S-6; S.S.316L → SS316L (non-API)
Mapping | Design Code → Pump Standard | "API 610 / IPS" → API 610 (IPS reference kept in source text)
Mapping | Driver (from Remarks) | Electric / Diesel / Portable parsed from Remarks "Driver:" text
Mapping | Price Basis → Price Source Type | FEED MTO → Historical Estimate; Inquiry → Budgetary Quote; Purchase price → PO
Mapping | Src AACE Class (verify) | Koopal FEED → 3; Gachsaran 4 Basic Design MTO → 4; Pazanan 2 Basic MTO → 4; CSV (no project) → blank. Original label kept in "Estimate Class (as stated in source)"
Mapping | Incoterm | Pazanan 2 EUR inquiries → FOB (sheet header "GOING UNIT PRICE FOB EUR"); others Not stated
New | Seal / Ex / VFD / NACE / Scope | Not stated in any source → "Not stated" (factor 1.00) – to be completed
Fix | Assumptions & FX (1405) | Circular reference B25 (=C25/D25) ↔ D25 (=C25/B25) removed: B25 = C25/1.1 per Maroon3 note
New | Escalation | PPI-based method from claude/pump-escalation-method.md, incl. 25,000 EUR floor; PPI table needs Eurostat values
QA | Rows 88, 89, 92, 93 | Reference currency EUR with price 1e8–3e8 → flagged "Check currency" (probably IRR) – not changed, verify against Koopal source
Update | Koopal Bangestan rows 59–78, 91 | NACE, Type, Material, Std, Q, Head, Ex (P-246), Incoterm, Scope TPI filled from KPL-476 R03 (PUMPS-B…(5), DESALTERS-B, STRIPPER-B, IWWTP-B, INS-PUMP-B, TOTAL (2)); evidence in cell comments; inferred cells yellow
Fix | Row 77 (P-144) | Pump type corrected: Centrifugal (assumed) → PD-Rotary (Twin Screw) per IWWTP-B (2) F17
Note | Seal (Plan 53B) | TK-154, P-154 A/B, F-161 serve a common Plan 53B sealing system; tag allocation not stated → Seal fields left Not stated
Update | Koopal Asmari / Common rows 41–58, 79–93 (excl. 91) | NACE (N, inferred – no MR-0175 in any -A/-C sheet), Type/Material/Std of package pumps, Q, Head, Ex (P-236), Incoterm, Scope TPI from KPL-476 R03; evidence in cell comments; inferred cells yellow
Fix | Rows 88, 89, 92, 93 (P-154, P-157, P-220, P-116) | Reference currency EUR → IRR (prices sit in the "Unit Price (Rials)" column U)
Fix | Row 92 (P-220) | Capacity 160 m³/h → 9.6 m³/h (source: 160 Lit/min)
Fix | Row 58 (P-134) | Pump type corrected: Centrifugal (assumed) → PD-Rotary (Twin Screw) per IWWTP-A (2) F17
Fix | Gachsaran 4 rows 15–35, 39, 40 | Reference price changed from IRR (stored as 1399) to the EUR base price found inside P.ME formulas (=EUR×per_Euro×USD_Change_IRR); Cost Year 1402 (inferred). Previous conversion with the 1399 FX rate overstated EUR ≈2.6×
Update | Gachsaran 4 rows 36–38 (fire pumps) | IRR constants kept; Cost Year 1399 → 1402 (inferred, PEP Rev.1402/05)
Update | Gachsaran 4 all pumps | Incoterm EXW, Scope TPI/Comm. spares/2-yr spares = N (inferred – carried as separate lines in Procurement sheet)
Note | Gachsaran 4 NACE | P.PI marks piping classes AN16/CN16 as NACE (sour process lines) but no pump-level NACE statement → pump NACE left Not stated
Note | FX 1402 | PEP implies EUR→IRR = 420,000×1.085 = 455,700; bank FX table 1402 has 529,500 – verify
Update | Pazanan 2 rows 94–114 | NACE from item descriptions (Y explicit for P-111/136/137/139/161/163/164; N inferred for the rest)
Fix | Rows 105, 113, 114 (P-163, P-210, P-211) | No quotation existed (all declined); the 1404 value was the 1393 R02 price × external factor. Reset to 1393 base price, Source Type = Historical Estimate, to avoid double escalation
Fix | Rows 113, 114 | Capacity 160 m³/h → 9.6 m³/h (source: 160 Lit/min)
New | Vendor_Register / Vendor_Quotes | 4 vendors and all Pazanan 2 quotations (incl. declined / no reply) loaded; Bid Count, Min/Max, Spread now live in Master
Update | Escalation_Index | PPI 1385–1405 filled from Pump_Escalation_Validation.xlsx (Indices C51:C71, EA20 C28.13, 2021=100, Jalali blend 0.79/0.21); 1405 is a forecast
New | Rows 129–146 | 18 Pazanan 2 R02 (1393) FOB records added (PUMPS AR8:AR26), paired with the 1404 inquiry records of the same tags
Note | Gachsaran 4 IRR cells | Converted with bank FX 1402; project rate 455,692 IRR/EUR and project IRR price recorded in cell comment (light-blue cells)
v6 Structure | Master Database | New column order (identification → key specs → supplementary specs → price → scope → source → calculations → control) with collapsible groups
v6 Removed | Unit, VFD, Motor Ex, Price Source Type, Src AACE Class, Bid Count, Min/Max Quote, Spread, Price Age, DQ Score, Usable For Class, Accuracy | Removed per organisation request; VFD and Ex factors removed from DRIVE_F, Estimator and Factors_ROT; Class_Matrix sheet removed
v6 New | Standards (combined), IPS Standard, Escalated USD, Price Basis (as stated in source) | Standards = Pump Standard + IPS + NACE + NFPA listing; Price Basis quotes the source basis and its class label
v6 Fix | Equipment Name | Duplicate sub-category text in parentheses removed (it equalled the sub-category full name in all records)
v6 Fix | Gachsaran 4 Pump Standard | "API 610" removed → Not stated (no standard given in PEP P.ME); Pump Family "Centrifugal" marked inferred (source: assumed)
v6 Fix | API 610 Type | Non-API pumps → N/A (non-API 610); Koopal P-270/P-271 → BB, P-272 → OH (per source text)
v6 Fix | Factors / material descriptions | Material class descriptions rewritten per API 610 Table H.1 (casing / impeller / rings / shaft)
v8 Layout | Seal columns / Vendor_Quotes | Seal Type and API 682 Category grouped (collapsed) with Pump Standard, IPS and NACE; API 682 Seal Plan stays visible. Vendor_Quotes: Equipment Name (auto) and Vendor Name (auto) added
v7 Removed | Category, Vendor_ID, NFPA 20 Listing | Category always ROT (covered by Sub-Category); no awarded vendor in any record; NFPA listing never stated
v7 Moved | Unit Price EUR / USD / IRR (source yr) | Moved next to Unit Price (Reference); Scope flags made collapsible
v7 Verified | All records | Field-by-field verification against the five source files – see Verification_Log
v7 Notes | Master / Factors_ROT / Dashboard | Sub-Category, API type and material notes moved to Master and Factors_ROT; Incoterm notes state what the price includes / excludes
v6 Data fix | Row 9 – Sub-Category | ROT-DRN → ROT-WAT
v6 Data fix | Row 11 – Service Fluid | Chemical → Diesel / Fuel Oil
v6 Data fix | Row 11 – API 610 Type | N/A → N/A (non-API 610)
v6 Data fix | Row 12 – Service Fluid | Chemical → Diesel / Fuel Oil
v6 Data fix | Row 12 – API 610 Type | N/A → N/A (non-API 610)
v6 Data fix | Row 13 – Service Fluid | Sludge → Process / Dilution Water
v6 Data fix | Row 13 – Pump Family | Jet / Eductor → Centrifugal
v6 Data fix | Row 15 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 16 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 17 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 18 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 19 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 20 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 21 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 22 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 23 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 24 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 25 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 26 – Sub-Category | ROT-INJ → ROT-AUX
v6 Data fix | Row 26 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 27 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 28 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 29 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 30 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 31 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 32 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 33 – Sub-Category | ROT-CRU → ROT-DRN
v6 Data fix | Row 33 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 34 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 35 – Service Fluid | Chemical → Diesel / Fuel Oil
v6 Data fix | Row 35 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 36 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 37 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 38 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 39 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 40 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 42 – Sub-Category | ROT-INJ → ROT-CRU
v6 Data fix | Row 42 – Service Fluid | Produced / Disposal Water → Crude Oil
v6 Data fix | Row 43 – Sub-Category | ROT-CRU → ROT-DRN
v6 Data fix | Row 43 – API 610 Type | N/A → N/A (non-API 610)
v6 Data fix | Row 50 – Sub-Category | ROT-CRU → ROT-DRN
v6 Data fix | Row 50 – API 610 Type | N/A → N/A (non-API 610)
v6 Data fix | Row 51 – Service Fluid | Process / Dilution Water → Oily Water / Drain
v6 Data fix | Row 57 – API 610 Type | N/A → N/A (non-API 610)
v6 Data fix | Row 58 – Sub-Category | ROT-CRU → ROT-DRN
v6 Data fix | Row 58 – API 610 Type | N/A → N/A (non-API 610)
v6 Data fix | Row 61 – Sub-Category | ROT-INJ → ROT-CRU
v6 Data fix | Row 61 – Service Fluid | Produced / Disposal Water → Crude Oil
v6 Data fix | Row 62 – Sub-Category | ROT-CRU → ROT-DRN
v6 Data fix | Row 62 – API 610 Type | N/A → N/A (non-API 610)
v6 Data fix | Row 69 – Sub-Category | ROT-CRU → ROT-DRN
v6 Data fix | Row 69 – API 610 Type | N/A → N/A (non-API 610)
v6 Data fix | Row 70 – Service Fluid | Process / Dilution Water → Oily Water / Drain
v6 Data fix | Row 76 – API 610 Type | N/A → N/A (non-API 610)
v6 Data fix | Row 77 – Sub-Category | ROT-CRU → ROT-DRN
v6 Data fix | Row 77 – API 610 Type | N/A → N/A (non-API 610)
v6 Data fix | Row 79 – API 610 Type | Not stated → N/A (non-API 610)
v6 Data fix | Row 80 – API 610 Type | Not stated → N/A (non-API 610)
v6 Data fix | Row 81 – Pump Family | Centrifugal - Vertical Sump → Centrifugal
v6 Data fix | Row 82 – Service Fluid | Chemical → Diesel / Fuel Oil
v6 Data fix | Row 82 – API 610 Type | Not stated → N/A (non-API 610)
v6 Data fix | Row 83 – Pump Family | Centrifugal - Vertical Sump → Centrifugal
v6 Data fix | Row 84 – API 610 Type | Not stated → BB (unspecified)
v6 Data fix | Row 85 – API 610 Type | Not stated → BB (unspecified)
v6 Data fix | Row 86 – API 610 Type | Not stated → OH (unspecified)
v6 Data fix | Row 87 – API 610 Type | Not stated → N/A (non-API 610)
v6 Data fix | Row 88 – API 610 Type | Not stated → N/A (non-API 610)
v6 Data fix | Row 89 – API 610 Type | Not stated → N/A (non-API 610)
v6 Data fix | Row 90 – API 610 Type | Not stated → N/A (non-API 610)
v6 Data fix | Row 91 – API 610 Type | Not stated → N/A (non-API 610)
v6 Data fix | Row 92 – Sub-Category | ROT-INJ → ROT-AUX
v6 Data fix | Row 92 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 92 – API 610 Type | N/A → N/A (non-API 610)
v6 Data fix | Row 93 – Sub-Category | ROT-WAT → ROT-AUX
v6 Data fix | Row 93 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 93 – API 610 Type | N/A → N/A (non-API 610)
v6 Data fix | Row 95 – API 610 Type | Not stated → N/A (non-API 610)
v6 Data fix | Row 99 – Sub-Category | ROT-CRU → ROT-DRN
v6 Data fix | Row 99 – API 610 Type | N/A → N/A (non-API 610)
v6 Data fix | Row 104 – Pump Family | Centrifugal - Vertical Sump → Centrifugal
v6 Data fix | Row 105 – Sub-Category | ROT-CRU → ROT-DRN
v6 Data fix | Row 105 – API 610 Type | N/A → N/A (non-API 610)
v6 Data fix | Row 106 – Service Fluid | Process / Dilution Water → Oily Water / Drain
v6 Data fix | Row 108 – Service Fluid | Chemical → Diesel / Fuel Oil
v6 Data fix | Row 108 – API 610 Type | Not stated → N/A (non-API 610)
v6 Data fix | Row 109 – API 610 Type | Not stated → N/A (non-API 610)
v6 Data fix | Row 113 – Sub-Category | ROT-INJ → ROT-AUX
v6 Data fix | Row 113 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 113 – API 610 Type | N/A → N/A (non-API 610)
v6 Data fix | Row 114 – Sub-Category | ROT-INJ → ROT-AUX
v6 Data fix | Row 114 – Pump Standard | API 610 → Not stated
v6 Data fix | Row 114 – API 610 Type | N/A → N/A (non-API 610)
v6 Data fix | Row 123 – Sub-Category | ROT-DRN → ROT-WAT
v6 Data fix | Row 125 – Service Fluid | Chemical → Diesel / Fuel Oil
v6 Data fix | Row 125 – API 610 Type | N/A → N/A (non-API 610)
v6 Data fix | Row 126 – Service Fluid | Chemical → Diesel / Fuel Oil
v6 Data fix | Row 126 – API 610 Type | N/A → N/A (non-API 610)
v6 Data fix | Row 127 – Service Fluid | Sludge → Process / Dilution Water
v6 Data fix | Row 127 – Pump Family | Jet / Eductor → Centrifugal
v6 Data fix | Row 130 – API 610 Type | Not stated → N/A (non-API 610)
v6 Data fix | Row 134 – Sub-Category | ROT-CRU → ROT-DRN
v6 Data fix | Row 134 – API 610 Type | N/A → N/A (non-API 610)
v6 Data fix | Row 139 – Pump Family | Centrifugal - Vertical Sump → Centrifugal
v6 Data fix | Row 140 – Service Fluid | Process / Dilution Water → Oily Water / Drain
v6 Data fix | Row 142 – Service Fluid | Chemical → Diesel / Fuel Oil
v6 Data fix | Row 142 – API 610 Type | Not stated → N/A (non-API 610)
v6 Data fix | Row 143 – API 610 Type | Not stated → N/A (non-API 610)
v6 Data fix | Row 1 – Diff. Head (m) | None → 95.8
v6 Data fix | Row 2 – Diff. Head (m) | None → 59.9
v6 Data fix | Row 3 – Diff. Head (m) | None → 34.8
v6 Data fix | Row 4 – Diff. Head (m) | None → 329.0
v6 Data fix | Row 5 – Diff. Head (m) | None → 311.3
v6 Data fix | Row 6 – Diff. Head (m) | None → 32.0
v6 Data fix | Row 7 – Diff. Head (m) | None → 36.2
v6 Data fix | Row 8 – Diff. Head (m) | None → 1383.0
v6 Data fix | Row 9 – Diff. Head (m) | None → 41.0
v6 Data fix | Row 10 – Diff. Head (m) | None → 120.0
v6 Data fix | Row 11 – Diff. Head (m) | None → 27.2
v6 Data fix | Row 12 – Diff. Head (m) | None → 40.8
v6 Data fix | Row 13 – Diff. Head (m) | None → 15.0
v6 Data fix | Row 14 – Diff. Head (m) | None → 18.0
v6 Data fix | Row 35 – Driver Type | Diesel Engine → Electric Motor
v6 Data fix | Row 54 – IPS Standard | None → IPS-G-PM-105
v6 Data fix | Row 55 – IPS Standard | None → IPS-G-PM-105
v6 Data fix | Row 56 – IPS Standard | None → IPS-G-PM-105
v6 Data fix | Row 57 – IPS Standard | None → IPS-M-PM-140
v6 Data fix | Row 58 – IPS Standard | None → IPS-G-PM-105
v6 Data fix | Row 73 – IPS Standard | None → IPS-G-PM-105
v6 Data fix | Row 74 – IPS Standard | None → IPS-G-PM-105
v6 Data fix | Row 75 – IPS Standard | None → IPS-G-PM-105
v6 Data fix | Row 76 – IPS Standard | None → IPS-M-PM-140
v6 Data fix | Row 77 – IPS Standard | None → IPS-G-PM-105
v6 Data fix | Row 88 – Equipment Name | Cooling Water (Pumps Seal System) Recycle Pumps → Cooling Water (Sealing System) Recycle Pumps
v6 Data fix | Row 89 – Equipment Name | Water Liquid Ring Return Pumps (Deaeration System) → Water Liquid Return Pumps (Deaeration System)
v6 Data fix | Row 115 – Diff. Head (m) | None → 95.8
v6 Data fix | Row 116 – Diff. Head (m) | None → 59.85
v6 Data fix | Row 117 – Diff. Head (m) | None → 34.75
v6 Data fix | Row 119 – Diff. Head (m) | None → 311.3
v6 Data fix | Row 120 – Diff. Head (m) | None → 32.0
v6 Data fix | Row 121 – Diff. Head (m) | None → 36.15
v6 Data fix | Row 122 – Diff. Head (m) | None → 51.5
v6 Data fix | Row 123 – Diff. Head (m) | None → 41.0
v6 Data fix | Row 124 – Diff. Head (m) | None → 120.0
v6 Data fix | Row 125 – Diff. Head (m) | None → 27.2
v6 Data fix | Row 126 – Diff. Head (m) | None → 40.8
v6 Data fix | Row 126 – Power (kW) | 0.8 → 0.83